LAPORAN UJI MINYAK TRAFO

di

UNIT JASA PEMBANGKIT

Yang dilakukan pada tanggal 27 November 2017

Untuk keadaan trafo bulan NOVEMBER 2017

Untuk pengganti pekerjaan – Mei 2017

TAHAP 1

Ref No : TXM/MKT-1200/SA/CI17048B

1.0 Table of Contents                                                                                                          Page

1.0        Specific Information                                                                                                    2

2.0        Our Comments and Recommendations of the Test Results  Analysis

-       Transformer Unit TRAFO 1 ESP UNIT 2 (S/N: 10037)                                            3

Test Certificate 17

-       Transformer Unit TRAFO 2 ESP UNIT 2 (S/N: 10036)                                            4

Test Certificate 18

-       Transformer Unit TRAFO 3 ESP UNIT 2 (S/N: 10033)                                            5

Test Certificate 19

-       Transformer Unit TRAFO 4 ESP UNIT 2 (S/N: 10032)                                            6

Test Certificate 20

-       Transformer Unit MAIN TRAFO UNIT 2 (S/N: 1006902)                                         7

Test Certificate 21

3.0        Summary of Recommendation                                                                                8

Ref No : TXM/MKT-1200/SA/CI17048B

1.0      Specific Information:

| No. | Unit No. | Serial Number | TC | Test Requested |
| --- | --- | --- | --- | --- |
| 1. | TRAFO 1 ESP UNIT 2 | 10037 | 17 | Acidity, Dielectric, Color, Visualization and Water Content |
| 2. | TRAFO 2 ESP UNIT 2 | 10036 | 18 | Acidity, Dielectric, Color, Visualization and Water Content |
| 3. | TRAFO 3 ESP UNIT 2 | 10033 | 19 | Acidity, Dielectric, Color, Visualization and Water Content |
| 4. | TRAFO 4 ESP UNIT 2 | 10032 | 20 | Acidity, Dielectric, Color, Visualization and Water Content |
| 5. | MAIN TRAFO UNIT 2 | 1006902 | 21 | Acidity, Dielectric, Color, Visualization and Water Content |

Note:

* OLTT+ consists of Liquid Screen Tests, Dissolved Gas Analysis (DGA), Water Content, Furan Analysis, Metals-in-Oil Analysis, Liquid Power Factors, and Inhibitor Content (DBPC).

** Liquid Screen Test consists of Acidity, Interfacial Tension (IFT), Dielectric, Colour, Specific Gravity, Visualization, and Sediment.

Ref No : TXM/MKT-1200/SA/CI17048B

2.0      Our Comments and Recommendations of The Test Results Analysis:

We  had  reviewed  each  laboratory  test  result  against  respective  benchmark parameter and following are our comments and recommendations.

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 1. | TRAFO 1 ESP UNIT 2 | 10037 | 17 |

A)  Analysis

-      Acidity of 0.020mgKOH/g is ACCEPTABLE.

-      Dielectric breakdown voltage of 48kV is ACCEPTABLE.

-      Colour of 1.0 utilizing ASTM D1500 standard is ACCEPTABLE.

-      Visualization of transformer oil is CLEAR, thus ACCEPTABLE.

-	Water Content in oil of 21ppm is QUESTIONABLE while moisture in solid insulation of 2.48% M/dw is graded as D. For this transformer, it is recommended to maintain the water content less than 20ppm. High level of moisture content will act as catalyst to the oxidation process.

B) Recommendation

-	Retest Water Content and Dielectric in 6 months to assess if corrective work on the transformer oil is required.

-	Other parameters: Do carry out *Liquid Screen Tests, Water Content, Furan  Analysis,  Metals-In-Oil,  Liquid  Power  Factor  and  Inhibitor

Content tests annually for Condition Monitoring purposes.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and

CENNIX LABORATORY (M) SDN BHD                                           17

(Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE             STATUS    OIL TEMP °C    W. TEMP °C       OIL LEVEL        PAINT       S. GEL              LEAKS

28/11/2017      OFFLINE

LIQUID SCREEN TEST DATA

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - TRAFO 1 ESP UNIT 2

LOCATION - OUTDOOR OTHER -

NAMEPLATE DATA

MFG                               - FUJIAN DATE MFG                    - 2010

MAIN TANK S/N            - 10037

KVA                               -

PRI                                 - 72000 V

380 V

|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | SEC - |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | SERVICES | ACID (mgKOH/gm) | IFT (mN/m) | DIEL (kV) | COLOUR | SP. GR. | VISUAL | ® SEDIMENT | KILOGRAMS EQUIP TYPE | - - |

28/11/2017       ROUTINE               0.020 AC                                          48 AC            1.0 AC                                        CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON     CARBON                                                                  TOTAL              TOTAL DATE     HYDROGEN  OXYGEN    NITROGEN   METHANE MONOXIDE  DIOXIDE  ETHANE ETHYLENE  ACETYLENE COMBUSTIBLE      GAS

RECOMMENDATION:

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM DATE            TEMP°C           PPM              %M/dw              GRADE

28/11/2017       27                  21                  2.48                   D

TRANSFORMER TRANS CLASS              - ONAN IMPEDENCE                 -

PHASE/CYCLE             - 3/50 Hz LIQUID TYPE                - OIL LITRES LIQUID             -

LTC MFG                       - LTC S/N                         - LTC FAB NO                 - LTC MODEL                  - LTC LITRES LIQUID     - LTC ENERGIZED          -

ADDITIONAL EQUIPMENT RADIATORS                  -

FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

CENNIX LABORATORY SDN BHD                                                 17

(Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

DATE              5H2F             2FOL             2FAL             2ACF             5M2F             TOTAL

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - TRAFO 1 ESP UNIT 2

LOCATION - OUTDOOR OTHER -

NAMEPLATE DATA

|  | MFG DATE MFG | - FUJIAN - 2010 |
| --- | --- | --- |
| RECOMMENDATION: | MAIN TANK S/N KVA | - 10037 - |
|  | PRI | - 72000 V |
|  | SEC | - 380 V |
|  | KILOGRAMS | - |
|  | EQUIP TYPE | - TRANSFORMER |
|  | TRANS CLASS | - ONAN |
|  | IMPEDENCE | - |
| METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM ® ® DATE ALUMINIUM IRON COPPER | PHASE/CYCLE LIQUID TYPE LITRES LIQUID | - 3/50 Hz - OIL - |
|  | LTC MFG | - |
|  | LTC S/N | - |
|  | LTC FAB NO | - |
|  | LTC MODEL | - |
|  | LTC LITRES LIQUID | - |
|  | LTC ENERGIZED | - |

LIQUID POWER FACTOR (ASTM D924)                                                                             INHIBITOR CONTENT, DBPC (ASTM D2668) DATE                       25°C                         100°C                                                                                  DATE                        %BY WEIGHT

ADDITIONAL EQUIPMENT

RADIATORS                  - FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

®

CORROSIVE SULFUR (ASTM 1275B)

®

PASSIVATOR COUNT, EXPRESSED IN PPM

DATE                   STATUS              CLASS                APPEARANCE                                                                                         DATE                   PPM

Ref No : TXM/MKT-1200/SA/CI17048B

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 2. | TRAFO 2 ESP UNIT 2 | 10036 | 18 |

A)  Analysis

-    Acidity of 0.048mgKOH/gm is ACCEPTABLE.

-    Dielectric of 55kV is ACCEPTABLE.

-    Colour of 1.0 utilizing ASTM D1500 standard is ACCEPTABLE.

-    Visualization of transformer oil is CLEAR, thus ACCEPTABLE.

-	Water  Content in oil of 13ppm is ACCEPTABLE while moisture in solid insulation of 1.53% M/dw is graded as C.  For this transformer, it is recommended to maintain the water content less than 20ppm.

B) Recommendation

-	Do carry-out *Liquid Screen, Liquid Power Factor, Inhibitor, Water Content, Metals-In-Oil, Furan Analysis & DGA periodically for Condition Monitoring purposes

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information herein

Page 4 of 8

CENNIX LABORATORY (M) SDN BHD                                           18

(Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE             STATUS    OIL TEMP °C    W. TEMP °C       OIL LEVEL        PAINT       S. GEL              LEAKS

28/11/2017      OFFLINE

LIQUID SCREEN TEST DATA

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - TRAFO 2 ESP UNIT 2

LOCATION - OTHER -

NAMEPLATE DATA

MFG                               - FUJIAN DATE MFG                    - 2010

MAIN TANK S/N            - 10036

KVA                               -

PRI                                 - 72000 V

380 V

|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | SEC - |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | SERVICES | ACID (mgKOH/gm) | IFT (mN/m) | DIEL (kV) | COLOUR | SP. GR. | VISUAL | ® SEDIMENT | KILOGRAMS EQUIP TYPE | - - |

28/11/2017       ROUTINE               0.048 AC                                          55 AC            1.0 AC                                        CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON     CARBON                                                                  TOTAL              TOTAL DATE     HYDROGEN  OXYGEN    NITROGEN   METHANE MONOXIDE  DIOXIDE  ETHANE ETHYLENE  ACETYLENE COMBUSTIBLE      GAS

RECOMMENDATION:

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM DATE            TEMP°C           PPM              %M/dw              GRADE

28/11/2017       28                  13                  1.53                   C

TRANSFORMER TRANS CLASS              - ONAN IMPEDENCE                 -

PHASE/CYCLE             - 3/50 Hz LIQUID TYPE                - OIL LITRES LIQUID             -

LTC MFG                       - LTC S/N                         - LTC FAB NO                 - LTC MODEL                  - LTC LITRES LIQUID     - LTC ENERGIZED          -

ADDITIONAL EQUIPMENT RADIATORS                  -

FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

CENNIX LABORATORY SDN BHD                                                 18

(Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

DATE              5H2F             2FOL             2FAL             2ACF             5M2F             TOTAL

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - TRAFO 2 ESP UNIT 2

LOCATION - OTHER -

NAMEPLATE DATA

|  | MFG DATE MFG | - FUJIAN - 2010 |
| --- | --- | --- |
| RECOMMENDATION: | MAIN TANK S/N KVA | - 10036 - |
|  | PRI | - 72000 V |
|  | SEC | - 380 V |
|  | KILOGRAMS | - |
|  | EQUIP TYPE | - TRANSFORMER |
|  | TRANS CLASS | - ONAN |
|  | IMPEDENCE | - |
| METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM ® ® DATE ALUMINIUM IRON COPPER | PHASE/CYCLE LIQUID TYPE LITRES LIQUID | - 3/50 Hz - OIL - |
|  | LTC MFG | - |
|  | LTC S/N | - |
|  | LTC FAB NO | - |
|  | LTC MODEL | - |
|  | LTC LITRES LIQUID | - |
|  | LTC ENERGIZED | - |

LIQUID POWER FACTOR (ASTM D924)                                                                             INHIBITOR CONTENT, DBPC (ASTM D2668) DATE                       25°C                         100°C                                                                                  DATE                        %BY WEIGHT

ADDITIONAL EQUIPMENT

RADIATORS                  - FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

®

CORROSIVE SULFUR (ASTM 1275B)

®

PASSIVATOR COUNT, EXPRESSED IN PPM

DATE                   STATUS              CLASS                APPEARANCE                                                                                         DATE                   PPM

Ref No : TXM/MKT-1200/SA/CI17048B

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 3. | TRAFO 3 ESP UNIT 2 | 10033 | 19 |

A)  Analysis

-	Acidity of 0.053mgKOH/g is QUESTIONABLE. This indicates the starting formation of oxidation by products in the oil.

-    Dielectric of 42kV is ACCEPTABLE.

-    Colour of 1.5 utilizing ASTM D1500 standard is ACCEPTABLE.

-    Visualization of transformer oil is CLEAR, thus ACCEPTABLE.

-	Water  Content in oil of 15ppm is ACCEPTABLE while moisture in solid insulation of 1.77% M/dw is graded as D.  For this transformer, it is recommended to maintain the water content less than 20ppm.

B) Recommendation

-	Retest Acidity and Interfacial Tension in 6 months to assess if the insulating oil deteriorate to a level that require corrective action to improve the oil quality.

-    Other parameters: Do carry out *Liquid Screen Tests, Water Content, Furan

Analysis, Metals-In-Oil, Liquid Power Factor and Inhibitor Content tests

annually for Condition Monitoring purposes.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information herein

Page 5 of 8

CENNIX LABORATORY (M) SDN BHD                                           19

(Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE             STATUS    OIL TEMP °C    W. TEMP °C       OIL LEVEL        PAINT       S. GEL              LEAKS

28/11/2017      OFFLINE

LIQUID SCREEN TEST DATA

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - TRAFO 3 ESP UNIT 2

LOCATION - OTHER -

NAMEPLATE DATA

MFG                               - FUJIAN DATE MFG                    - 2010

MAIN TANK S/N            - 10033

KVA                               -

PRI                                 - 72000 V

380 V

|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | SEC - |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | SERVICES | ACID (mgKOH/gm) | IFT (mN/m) | DIEL (kV) | COLOUR | SP. GR. | VISUAL | ® SEDIMENT | KILOGRAMS EQUIP TYPE | - - |

28/11/2017       ROUTINE               0.053 QU                                         42 AC            1.5 AC                                        CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON     CARBON                                                                  TOTAL              TOTAL DATE     HYDROGEN  OXYGEN    NITROGEN   METHANE MONOXIDE  DIOXIDE  ETHANE ETHYLENE  ACETYLENE COMBUSTIBLE      GAS

RECOMMENDATION:

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM DATE            TEMP°C           PPM              %M/dw              GRADE

28/11/2017       28                  15                  1.77                   D

TRANSFORMER TRANS CLASS              - ONAN IMPEDENCE                 -

PHASE/CYCLE             - 3/50 Hz LIQUID TYPE                - OIL LITRES LIQUID             -

LTC MFG                       - LTC S/N                         - LTC FAB NO                 - LTC MODEL                  - LTC LITRES LIQUID     - LTC ENERGIZED          -

ADDITIONAL EQUIPMENT RADIATORS                  -

FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

CENNIX LABORATORY SDN BHD                                                 19

(Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

DATE              5H2F             2FOL             2FAL             2ACF             5M2F             TOTAL

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - TRAFO 3 ESP UNIT 2

LOCATION - OTHER -

NAMEPLATE DATA

|  | MFG DATE MFG | - FUJIAN - 2010 |
| --- | --- | --- |
| RECOMMENDATION: | MAIN TANK S/N KVA | - 10033 - |
|  | PRI | - 72000 V |
|  | SEC | - 380 V |
|  | KILOGRAMS | - |
|  | EQUIP TYPE | - TRANSFORMER |
|  | TRANS CLASS | - ONAN |
|  | IMPEDENCE | - |
| METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM ® ® DATE ALUMINIUM IRON COPPER | PHASE/CYCLE LIQUID TYPE LITRES LIQUID | - 3/50 Hz - OIL - |
|  | LTC MFG | - |
|  | LTC S/N | - |
|  | LTC FAB NO | - |
|  | LTC MODEL | - |
|  | LTC LITRES LIQUID | - |
|  | LTC ENERGIZED | - |

LIQUID POWER FACTOR (ASTM D924)                                                                             INHIBITOR CONTENT, DBPC (ASTM D2668) DATE                       25°C                         100°C                                                                                  DATE                        %BY WEIGHT

ADDITIONAL EQUIPMENT

RADIATORS                  - FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

®

CORROSIVE SULFUR (ASTM 1275B)

®

PASSIVATOR COUNT, EXPRESSED IN PPM

DATE                   STATUS              CLASS                APPEARANCE                                                                                         DATE                   PPM

Ref No : TXM/MKT-1200/SA/CI17048B

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 4. | TRAFO 4 ESP UNIT 2 | 10032 | 20 |

A)  Analysis

-    Acidity of 0.020mgKOH/g is ACCEPTABLE.

-    Dielectric of 62kV is ACCEPTABLE.

-    Colour of 1.0 utilizing ASTM D1500 standard is ACCEPTABLE.

-    Visualization of transformer oil is CLEAR, thus ACCEPTABLE.

-	Water  Content in oil of 16ppm is ACCEPTABLE while moisture in solid insulation of 1.89% M/dw is graded as D.  For this transformer, it is recommended to maintain the water content less than 20ppm.

B) Recommendation

-	Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-In- Oil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information herein

Page 6 of 8

CENNIX LABORATORY (M) SDN BHD                                           20

(Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE             STATUS    OIL TEMP °C    W. TEMP °C       OIL LEVEL        PAINT       S. GEL              LEAKS

28/11/2017      OFFLINE

LIQUID SCREEN TEST DATA

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - TRAFO 4 ESP UNIT 2

LOCATION - OTHER -

NAMEPLATE DATA

MFG                               - FUJIAN DATE MFG                    - 2010

MAIN TANK S/N            - 10032

KVA                               -

PRI                                 - 72000 V

380 V

|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | SEC - |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | SERVICES | ACID (mgKOH/gm) | IFT (mN/m) | DIEL (kV) | COLOUR | SP. GR. | VISUAL | ® SEDIMENT | KILOGRAMS EQUIP TYPE | - - |

28/11/2017       ROUTINE               0.020 AC                                          62 AC            1.0 AC                                        CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON     CARBON                                                                  TOTAL              TOTAL DATE     HYDROGEN  OXYGEN    NITROGEN   METHANE MONOXIDE  DIOXIDE  ETHANE ETHYLENE  ACETYLENE COMBUSTIBLE      GAS

RECOMMENDATION:

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM DATE            TEMP°C           PPM              %M/dw              GRADE

28/11/2017       28                  16                  1.89                   D

TRANSFORMER TRANS CLASS              - ONAN IMPEDENCE                 -

PHASE/CYCLE             - 3/50 Hz LIQUID TYPE                - OIL LITRES LIQUID             -

LTC MFG                       - LTC S/N                         - LTC FAB NO                 - LTC MODEL                  - LTC LITRES LIQUID     - LTC ENERGIZED          -

ADDITIONAL EQUIPMENT RADIATORS                  -

FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

CENNIX LABORATORY SDN BHD                                                 20

(Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

DATE              5H2F             2FOL             2FAL             2ACF             5M2F             TOTAL

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - TRAFO 4 ESP UNIT 2

LOCATION - OTHER -

NAMEPLATE DATA

|  | MFG DATE MFG | - FUJIAN - 2010 |
| --- | --- | --- |
| RECOMMENDATION: | MAIN TANK S/N KVA | - 10032 - |
|  | PRI | - 72000 V |
|  | SEC | - 380 V |
|  | KILOGRAMS | - |
|  | EQUIP TYPE | - TRANSFORMER |
|  | TRANS CLASS | - ONAN |
|  | IMPEDENCE | - |
| METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM ® ® DATE ALUMINIUM IRON COPPER | PHASE/CYCLE LIQUID TYPE LITRES LIQUID | - 3/50 Hz - OIL - |
|  | LTC MFG | - |
|  | LTC S/N | - |
|  | LTC FAB NO | - |
|  | LTC MODEL | - |
|  | LTC LITRES LIQUID | - |
|  | LTC ENERGIZED | - |

LIQUID POWER FACTOR (ASTM D924)                                                                             INHIBITOR CONTENT, DBPC (ASTM D2668) DATE                       25°C                         100°C                                                                                  DATE                        %BY WEIGHT

ADDITIONAL EQUIPMENT

RADIATORS                  - FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

®

CORROSIVE SULFUR (ASTM 1275B)

®

PASSIVATOR COUNT, EXPRESSED IN PPM

DATE                   STATUS              CLASS                APPEARANCE                                                                                         DATE                   PPM

Ref No : TXM/MKT-1200/SA/CI17048B

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 5. | MAIN TRAFO UNIT 2 | 1006902 | 21 |

A)  Analysis

-    Acidity of 0.008mgKOH/g is ACCEPTABLE.

-    Dielectric of 70kV is ACCEPTABLE.

-    Colour of 0.5 utilizing ASTM D1500 standard is ACCEPTABLE.

-    Visualization of transformer oil is CLEAR, thus ACCEPTABLE.

-	Water Content in oil of 16ppm is UNACCEPTABLE while moisture in solid insulation of 1.04% M/dw is graded as B.  For this transformer, it is recommended to maintain the water content less than 20ppm.

B) Recommendation

-	Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-In- Oil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information herein

Page 7 of 8

CENNIX LABORATORY (M) SDN BHD                                           21

(Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE             STATUS    OIL TEMP °C    W. TEMP °C       OIL LEVEL        PAINT       S. GEL              LEAKS

27/11/2017      ONLINE              50                    55

LIQUID SCREEN TEST DATA

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - MAIN TRAFO UNIT 2

LOCATION - OUTDOOR OTHER -

NAMEPLATE DATA

MFG                               - WOLONG DATE MFG                    - 2011

MAIN TANK S/N            - 1006902

KVA                               - 33000

PRI                                 - 170000 V

|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | SEC - 6300 V |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | SERVICES | ACID (mgKOH/gm) | IFT (mN/m) | DIEL (kV) | COLOUR | SP. GR. | VISUAL | ® SEDIMENT | KILOGRAMS EQUIP TYPE | - 81000 - TRAN |

27/11/2017       ROUTINE               0.008 AC                                          70 AC            0.5 AC                                        CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON     CARBON                                                                  TOTAL              TOTAL DATE     HYDROGEN  OXYGEN    NITROGEN   METHANE MONOXIDE  DIOXIDE  ETHANE ETHYLENE  ACETYLENE COMBUSTIBLE      GAS

RECOMMENDATION:

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM DATE            TEMP°C           PPM              %M/dw              GRADE

27/11/2017       37                  16                  1.04                   B

SFORMER TRANS CLASS              - ONAF IMPEDENCE                 - 13.03% PHASE/CYCLE             - 3/50 Hz

LIQUID TYPE                - OIL LITRES LIQUID             - 11160

LTC MFG                       - LTC S/N                         - LTC FAB NO                 - LTC MODEL                  - LTC LITRES LIQUID     - LTC ENERGIZED          -

ADDITIONAL EQUIPMENT RADIATORS                  -

FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

CENNIX LABORATORY SDN BHD                                                 21

(Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

DATE              5H2F             2FOL             2FAL             2ACF             5M2F             TOTAL

DATE PRINTED 19/12/2017

ID# - 601669

CUST - PT IP UJP PLTU JERANJANG

SUB NAME -

CITY - MATARAM LOMBOK UNIT# - MAIN TRAFO UNIT 2

LOCATION - OUTDOOR OTHER -

NAMEPLATE DATA

|  | MFG DATE MFG | - WOLONG - 2011 |
| --- | --- | --- |
|  | MAIN TANK S/N | - 1006902 |
| RECOMMENDATION: | KVA | - 33000 |
|  | PRI | - 170000 V |
|  | SEC | - 6300 V |
|  | KILOGRAMS | - 81000 |
|  | EQUIP TYPE | - TRANSFORMER |
|  | TRANS CLASS | - ONAF |
|  | IMPEDENCE | - 13.03% |
| METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM ® ® DATE ALUMINIUM IRON COPPER | PHASE/CYCLE LIQUID TYPE LITRES LIQUID | - 3/50 Hz - OIL - 11160 |
|  | LTC MFG | - |
|  | LTC S/N | - |
|  | LTC FAB NO | - |
|  | LTC MODEL | - |
|  | LTC LITRES LIQUID | - |
|  | LTC ENERGIZED | - |

LIQUID POWER FACTOR (ASTM D924)                                                                             INHIBITOR CONTENT, DBPC (ASTM D2668) DATE                       25°C                         100°C                                                                                  DATE                        %BY WEIGHT

ADDITIONAL EQUIPMENT

RADIATORS                  - FANS                             - H2O COOLED               - OIL PUMPS                   - TOP FPV                       - BOTTOM FPV               - BUCHOLZ - CONSERVATOR           - LTC COMPARTMENT   - BUSHING LOC              - FREE BREATHER        - HOSE LENGTH             - POWER AVAILABLE     -

®

CORROSIVE SULFUR (ASTM 1275B)

®

PASSIVATOR COUNT, EXPRESSED IN PPM

DATE                   STATUS              CLASS                APPEARANCE                                                                                         DATE                   PPM

Ref No : TXM/MKT-1200/SA/CI17048B

3.0      Summary of Our Comments & Recommendations:

| No. | TX Unit No. | Serial No. | TC | Recommendation |
| --- | --- | --- | --- | --- |
| 1. | TRAFO 1 ESP UNIT 2 | 10037 | 17 |  Retest 6 months: Dielectric and Water Content  Other parameters: Periodic condition monitoring |
| 2. | TRAFO 2 ESP UNIT 2 | 10036 | 18 |  Periodic condition monitoring |
| 3. | TRAFO 3 ESP UNIT 2 | 10033 | 19 |  Retest 6 months: Acidity and IFT  Other parameters: Periodic condition monitoring |
| 4. | TRAFO 4 ESP UNIT 2 | 10032 | 20 |  Periodic condition monitoring |
| 5. | MAIN TRAFO UNIT 2 | 1006902 | 21 |  Periodic condition monitoring |

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information herein

Page 8 of 8

| no | Test Cer. | Date Test | nama unit |  | Serial number | thn opr | Jumlah minyak, liter | Buatan | hasil test laboratorium cennix |  |  |  |  |  |  |  |  | MALAYSIAN LAB RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | acid | ift | diel. | color | spec. Graf. | visual | sedi. | moisture |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ppm | grade |  |
| Standard yang dipakai |  |  |  |  |  |  |  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | ASTM D1533 |  |  |
|  | BATASAN OPERASI |  |  |  |  |  |  |  | < 0,06 | > 32 | > 30 | < 3,5 | > 0,84 | C |  | < 20 |  |  |
| 1 | 17 | 27/11/17 | Trafo 1 ESP | 2 | 10037 | 1010 | 731 | Fujian | 0,020 |  | 48 | 1,0 |  | C |  | 21 | D | Retest 6 months: Dielectric and Water Content |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Other parameters: Periodic Condition Monitoring |
| 2 | 18 | 27/11/17 | Trafo 2 ESP | 2 | 10036 | 1010 | 731 | Fujian | 0,048 |  | 55 | 1,0 |  | C |  | 13 | C | Periodic condition monitoring |
| 3 | 19 | 27/11/17 | Trafo 3 ESP | 2 | 10033 | 1010 | 731 | Fujian | 0,053 |  | 42 | 1,5 |  | C |  | 15 | D | Retest 6 months: Acidity and IFT |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Other parameters: Periodic Condition Monitoring |
| 4 | 20 | 27/11/17 | Trafo 4 ESP | 2 | 10032 | 1010 | 731 | Fujian | 0,020 |  | 62 | 1,0 |  | C |  | 16 | D | Periodic condition monitoring |
| 5 | 21 | 27/11/17 | Main Trafo | 2 | 1006902 | 2011 | 11.160 | Wolong | 0,008 |  | 70 | 0,5 |  | C |  | 16 | B | Periodic condition monitoring |

Summary by Soetjahjono

TxM Indonesia

PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION

Kondisi semua trafo ESP (Tc 17, 18, 19, 20) Grade Moisture rendah, yang artinya kandungan air dalam isolasi kertas cukup tinggi. Kami sarankan untuk dimonitor dengan test DGA agar bisa diantisipasi jika ada kondisi gangguan thermal yang terjadi pada trafo trafo tersebut.