LAPORAN UJI MINYAK TRAFO

di

UNIT JASA PEMBANGKIT

# JERANJANG

Yang dilakukan pada tanggal 20 AGUSTUS 2019

## Untuk keadaan trafo periode 20 Agustus ~ 14 September  2019

Ref No : TXM/MKT-1200/SA/CI19034

1.0 Table of Contents 	Page

1.0 	Specific Information 	3

2.0 	Our Comments and Recommendations of the Test Results  Analysis

- Transformer Unit MAIN TRAFO UNIT 1 (S/N: 100691) 	5

Test Certificate 4

- Transformer Unit TRAFO 1 ESP UNIT 1 (S/N: 10937) 	6

Test Certificate 5

- Transformer Unit TRAFO 2 ESP UNIT 1 (S/N: 10035) 	7

Test Certificate 6

- Transformer Unit TRAFO 3 ESP UNIT 1 (S/N: 10031) 	8

Test Certificate 7

- Transformer Unit TRAFO 4 ESP UNIT 1 (S/N: 10034) 	9

Test Certificate 8

- Transformer Unit MAIN TRAFO UNIT 3 (S/N: 3011160192) 	10

Test Certificate 23

- Transformer Unit UAT 3 (S/N: PX18-0082) 	11

Test Certificate 22

- Transformer Unit TRAFO 1 ESP UNIT 3 (S/N: 0073084208) 	12

Test Certificate 11

- Transformer Unit TRAFO 2 ESP UNIT 3 (S/N: 0070084208) 	13

Test Certificate 12

- Transformer Unit TRAFO 3 ESP UNIT 3 (S/N: 0072084208) 	14

Test Certificate 13

- Transformer Unit TRAFO 4 UNIT 3 (S/N: 0071084208) 	15

Test Certificate 14

- Transformer Unit ASH HANDLING-1 (S/N: 10820108) 	16

Test Certificate 15

- Transformer Unit ASH HANDLING-2 (S/N: 10820107) 	17

Test Certificate 16

- Transformer Unit TRAFO 1 ESP UNIT 2 (S/N: 10037) 	18

Test Certificate 17

- Transformer Unit TRAFO 2 ESP UNIT 2 (S/N: 10036) 	19

Test Certificate 18

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the

Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

- Transformer Unit TRAFO 3 ESP UNIT 2 (S/N: 10033) 	20

Test Certificate 19

- Transformer Unit TRAFO 4 ESP UNIT 2 (S/N: 10032) 	21

Test Certificate 20

- Transformer Unit MAIN TRAFO UNIT 2 (S/N: 1006902) 	22

Test Certificate 21

3.0 	Summary of Recommendation 	23

.

1.0 	Specific Information:

| No. | Unit No. | Serial Number | TC | Test Requested |
| --- | --- | --- | --- | --- |
| 1. | MAIN TRAFO UNIT 1 | 100691 | 4 | Acidity, Dielectric, Color, Visualization and Water Content |
| 2. | TRAFO 1 ESP UNIT 1 | 10937 | 5 | Acidity, Dielectric, Color, Visualization and Water Content |
| 3. | TRAFO 2 ESP UNIT 1 | 10035 | 6 | Acidity, Dielectric, Color, Visualization and Water Content |
| 4. | TRAFO 3 ESP UNIT 1 | 10031 | 7 | Acidity, Dielectric, Color, Visualization and Water Content |
| 5. | TRAFO 4 ESP UNIT 1 | 10034 | 8 | Acidity, Dielectric, Color, Visualization and Water Content |
| 6. | MAIN TRAFO UNIT 3 | 3011160192 | 23 | Acidity, Dielectric, Color, Visualization and Water Content |
| 7. | UAT 3 | PX18-0082 | 22 | Acidity, Dielectric, Color, Visualization and Water Content |
| 8. | TRAFO 1 ESP UNIT 3 | 0073084208 | 11 | Acidity, Dielectric, Color, Visualization and Water Content |
| 9. | TRAFO 2 ESP UNIT 3 | 0070084208 | 12 | Acidity, Dielectric, Color, Visualization and Water Content |
| 10. | TRAFO 3 ESP UNIT 3 | 0072084208 | 13 | Acidity, Dielectric, Color, Visualization and Water Content |
| 11. | TRAFO 4 UNIT 3 | 0071084208 | 14 | Acidity, Dielectric, Color, Visualization and Water Content |
| 12. | ASH HANDLING-1 | 10820108 | 15 | Acidity, Dielectric, Color, Visualization and Water Content |
| 13. | ASH HANDLING-2 | 10820107 | 16 | Acidity, Dielectric, Color, Visualization and Water Content |
| 14. | TRAFO 1 ESP UNIT 2 | 10037 | 17 | Acidity, Dielectric, Color, Visualization and Water Content |
| 15. | TRAFO 2 ESP UNIT 2 | 10036 | 18 | Acidity, Dielectric, Color, Visualization and Water Content |
| 16. | TRAFO 3 ESP UNIT 2 | 10033 | 19 | Acidity, Dielectric, Color, Visualization and Water Content |
| 17. | TRAFO 4 ESP UNIT 2 | 10032 | 20 | Acidity, Dielectric, Color, Visualization and Water Content |

| No. | Unit No. | Serial Number | TC | Test Requested |
| --- | --- | --- | --- | --- |
| 18. | MAIN TRAFO UNIT 2 | 1006902 | 21 | Acidity, Dielectric, Color, Visualization and Water Content |

Note:

* OLTT+ consists of Liquid Screen Tests, Dissolved Gas Analysis (DGA), Water     Content, Furan Analysis, Metals-in-Oil Analysis, Liquid Power Factors, and Inhibitor       Content (DBPC).

** Liquid Screen Test consists of Acidity, Interfacial Tension (IFT), Dielectric, Colour,          Specific Gravity, Visualization, and Sediment.

Ref No : TXM/MKT-1200/SA/CI19034

2.0 Our Comments and Recommendations of The Test Results Analysis:  We had reviewed each laboratory test result against respective benchmark parameter and following are our comments and recommendations.

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 1. | MAIN TRAFO UNIT 1 | 100691 | 4 |

A) Analysis

- Acidity of 0.014mgKOH/g is ACCEPTABLE.

- Dielectric of 61kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 7ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 0.46% M/dw is graded as A. For this transformer, it is recommended to maintain water content in oil at less than 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

ONLINE	GOOD

25/08/2018	OFFLINE

25/09/2018	ONLINE

23/10/2018	ONLINE

22/11/2018	ONLINE

08/12/2018	ONLINE

21/05/2019	ONLINE

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	ONLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.014 AC	 	86 AC	   0.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.017 AC	 	90 AC	   0.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.014 AC	 	96 AC	   0.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.014 AC	 	83 AC	   0.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.014 AC	 	73 AC	   0.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.014 AC	 	75 AC	   0.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.014 AC	 	71 AC	   0.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.017 AC	41.3 AC	66 AC	   0.5 AC	     	0.8789 AC	CLEAR AC

25/07/2019	ROUTINE	    0.014 AC	 	79 AC	   0.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.014 AC	 	61 AC	   0.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	147	9471	43278	32	655	2728	4	5	ND	843	56320

06/12/2017	183	12895	43794	39	715	3166	5	5	ND	947	60802

28/06/2018	176	11044	46776	41	758	3393	5	6	ND	986	62199

20/06/2019	18	19122	60738	26	756	3272	2	3	ND	805	83937

RECOMMENDATION:

GAS LEVELS HAVE REMAINED STABLE. PROCEED WITH ANNUAL MONITORING.

32	6	0.57	A

30	6	0.63	A

38	7	0.46	A

44	8	0.36	A

41	9	0.45	A

41	8	0.40	A

- 8	0.52	A

- 7	0.38	A

38	8	0.52	A

38	7	0.46	A

4

### UNIT# - MAIN TRAFO UNIT 1

LOCATION - OUTDOOR OTHER -

#### NAMEPLATE DATA

| MFG | - WOLONG |
| --- | --- |
| DATE MFG | - 2011 |
| MAIN TANK S/N | - 100691 |
| KVA | - 40000 |
| PRI | - 165000 V |
| SEC | - 6300 V |
| KILOGRAMS | - 81000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - OFAF |
| IMPEDENCE | - 13.1% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 30857 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - YES H2O COOLED	 - NO OIL PUMPS	 - YES TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - YES BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

#### DATE	SERVICE

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 2. | TRAFO 1 ESP UNIT 1 | 10937 | 5 |

A) Analysis

- Acidity of 0.017mgKOH/g is ACCEPTABLE.

- Dielectric of 56kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water content in oil of 16ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.68% M/dw is graded as C. For this transformer, it is advisable to maintain the water content level below 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

6

25/08/2018	OFFLINE

25/09/2018	ONLINE

23/10/2018	ONLINE

22/11/2018	ONLINE

08/12/2018	OFFLINE

21/05/2019	ONLINE

20/06/2019	ONLINE

25/07/2019	OFFLINE

20/08/2019	OFFLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.073 QU	 	38 AC	   1.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.020 AC	 	71 AC	   0.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.017 AC	 	63 AC	   0.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.020 AC	 	49 AC	   0.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.017 AC	 	30 AC	   0.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.017 AC	 	41 AC	   0.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.017 AC	 	40 AC	   0.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.017 AC	38.7 AC	34 AC	   0.5 AC	     	0.8747 AC	CLEAR AC

25/07/2019	ROUTINE	    0.017 AC	 	61 AC	   0.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.017 AC	 	56 AC	   0.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	35	20494	67487	4	69	1143	ND	1	ND	109	89233

06/12/2017	39	19933	67198	4	83	1261	ND	1	ND	127	88519

28/06/2018	44	20039	64529	4	119	1696	ND	2	ND	169	86433

20/06/2019	22	27043	68613	5	36	689	ND	ND	ND	63	96408

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

29	19	2.00	D 32	12	1.14	B

35	18	1.28	B

40	24	1.32	B 37	23	1.50	C

32	18	1.71	D 39	22	1.21	B 38	23	1.50	C

29	18	1.89	D

29	16	1.68	C

5

### UNIT# - TRAFO 1 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

#### NAMEPLATE DATA

| MFG | - FUJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 10937 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 380 V |
| KILOGRAMS | - 1000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 630 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

#### DATE	SERVICE 01/08/2018 CHANGED OIL

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 3. | TRAFO 2 ESP UNIT 1 | 10035 | 6 |

A) Analysis

- Acidity of 0.020mgKOH/g is ACCEPTABLE.

- Dielectric of 51kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water content in oil of 15ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.58% M/dw is graded as C. For this transformer, it is advisable to maintain the water content level below 20ppm.

B) Recommendation

- Based on previous oil analysis, the IFT of the oil is unfavorable. It is recommended to perform Transformer Oil Regeneration on this unit. Transformer oil regeneration at this stage of contamination will effectively remove unwanted oxidation byproducts from the insulating oil. This process will restore the oil back to its original quality, thus protecting the paper insulation and extending the transformer serviceable lifespan. Furthermore, oil inhibitor 2,6-DBPC and passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

7

25/08/2018	OFFLINE

25/09/2018	OFFLINE

23/10/2018	OFFLINE

22/11/2018	OFFLINE

08/12/2018	OFFLINE

21/05/2019	OFFLINE

20/06/2019	ONLINE

25/07/2019	OFFLINE

20/08/2019	OFFLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.062 QU	 	47 AC	   1.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.022 AC	 	56 AC	   0.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.020 AC	 	67 AC	   0.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.020 AC	 	71 AC	   0.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.020 AC	 	63 AC	   0.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.020 AC	 	51 AC	   0.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.020 AC	 	71 AC	   0.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.020 AC	27.9 UN	68 AC	   0.5 AC	     	0.8658 AC	CLEAR AC

25/07/2019	ROUTINE	    0.022 AC	 	67 AC	   0.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.020 AC	 	51 AC	   0.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	27	18639	66781	3	64	1106	ND	1	ND	95	86621

06/12/2017	20	19360	61590	3	45	728	ND	1	ND	69	81747

28/06/2018	22	22494	64443	4	57	789	ND	ND	ND	83	87809

20/06/2019	23	17710	61707	5	23	842	ND	ND	ND	51	80310

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

- 15	1.58	C 31	13	1.24	B

- 11	1.04	B

33	14	1.15	B 34	18	1.48	C 33	14	1.15	B

37	15	0.98	B

37	17	1.11	B 30	15	1.58	C

29	15	1.58	C

6

### UNIT# - TRAFO 2 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

#### NAMEPLATE DATA

| MFG | - FUJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 10035 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 380 V |
| KILOGRAMS | - 1000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 630 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

#### DATE	SERVICE 01/08/2018 CHANGED OIL

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 4. | TRAFO 3 ESP UNIT 1 | 10031 | 7 |

A) Analysis

- Acidity of 0.051mgKOH/gm is QUESTIONABLE. Although the level remained stable, the oil are containing oxidation by-products. These oxidation by-products are depositing and degrading the oil as well as the paper insulation. Therefore, removal of these contaminations are highly recommended.

- Dielectric of 43kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water content in oil of 18ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.71% M/dw is graded as D. For this transformer, it is advisable to maintain the water content level below 20ppm.

B) Recommendation

- Based on previous oil analysis, the IFT of the oil is unfavorable. Together with the high level of Acidity, it is recommended to perform Transformer Oil Regeneration on this unit. Transformer oil regeneration at this stage of contamination will effectively remove unwanted oxidation byproducts from the insulating oil. This process will restore the oil back to its original quality, thus protecting the paper insulation and extending the transformer serviceable lifespan. Furthermore, oil inhibitor 2,6-DBPC and passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

8

25/08/2018	OFFLINE

25/09/2018	OFFLINE

23/10/2018	ONLINE

22/11/2018	OFFLINE

08/12/2018	OFFLINE

21/05/2019	ONLINE

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	ONLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.051 QU	 	64 AC	   1.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.056 QU	 	57 AC	   1.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.051 QU	 	46 AC	   1.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.056 QU	 	44 AC	   1.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.056 QU	 	39 AC	   1.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.056 QU	 	39 AC	   1.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.051 QU	 	33 AC	   1.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.051 QU	29.6 QU	30 AC	   1.5 AC	     	0.8689 AC	CLEAR AC

25/07/2019	ROUTINE	    0.056 QU	 	48 AC	   1.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.051 QU	 	43 AC	   1.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	32	15273	65111	5	95	1002	ND	2	ND	134	81520

06/12/2017	7	14730	65738	3	42	617	ND	ND	ND	52	81137

28/06/2018	9	17958	66007	4	46	781	ND	1	ND	60	84806

20/06/2019	16	17771	65478	6	73	829	ND	1	ND	96	84174

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

30	17	1.78	D

30	15	1.58	C

32	21	2.00	D

36	20	1.42	C

36	22	1.56	C

- 20	1.42	C 36	19	1.35	B

- 19	1.35	B 31	15	1.42	C

32	18	1.71	D

7

### UNIT# - TRAFO 3 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

#### NAMEPLATE DATA

| MFG | - FUJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 10031 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 380 V |
| KILOGRAMS | - 1000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 630 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

#### DATE	SERVICE

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 5. | TRAFO 4 ESP UNIT 1 | 10034 | 8 |

A) Analysis

- Acidity of 0.017mgKOH/g is ACCEPTABLE.

- Dielectric of 45kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water content in oil of 16ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.31% M/dw is graded as B. For this transformer, it is advisable to maintain the water content level below 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

9

25/08/2018	OFFLINE

25/09/2018	OFFLINE

23/10/2018	ONLINE

22/11/2018	OFFLINE

08/12/2018	OFFLINE

21/05/2019	OFFLINE

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	OFFLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.039 AC	 	50 AC	   1.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.017 AC	 	61 AC	   0.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.014 AC	 	45 AC	   0.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.014 AC	 	52 AC	   0.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.014 AC	 	44 AC	   0.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.014 AC	 	47 AC	   0.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.014 AC	 	41 AC	   0.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.014 AC	38.6 AC	45 AC	   0.5 AC	     	0.8775 AC	CLEAR AC

25/07/2019	ROUTINE	    0.014 AC	 	67 AC	   0.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.017 AC	 	45 AC	   0.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	13	12265	66770	5	172	1206	ND	8	ND	198	80439

06/12/2017	8	13331	63527	3	70	720	ND	1	ND	82	77660

28/06/2018	9	17962	64248	4	75	1054	ND	2	ND	90	83354

20/06/2019	11	15056	64828	5	11	951	ND	ND	ND	27	80862

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

31	19	1.80	D

30	14	1.47	C

30	20	2.10	D 41	21	1.05	B 38	21	1.37	C 38	20	1.30	B

- 19	1.35	B

- 19	1.24	B 32	16	1.52	C 33	16	1.31	B

8

### UNIT# - TRAFO 4 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

#### NAMEPLATE DATA

| MFG | - FUJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 10034 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 380 V |
| KILOGRAMS | - 1000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 630 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

#### DATE	SERVICE 01/08/2018 CHANGED OIL

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 6. | MAIN TRAFO UNIT 3 | 3011160192 | 23 |

A) Analysis

- Acidity of 0.011mgKOH/g is ACCEPTABLE.

- Dielectric of 78kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 6ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 0.33% M/dw is graded as A. For this transformer, it is recommended to maintain water content in oil at less than 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes

10

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	ONLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

21/05/2019	ROUTINE	    0.011 AC	 	93 AC	   0.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.011 AC	40.6 AC	83 AC	   0.5 AC	     	0.8786 AC	CLEAR AC

25/07/2019	ROUTINE	    0.014 AC	 	87 AC	   0.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.011 AC	 	78 AC	   0.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

20/06/2019	3	9903	31346	6	156	369	ND	ND	ND	165	41783

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

DATE

21/05/2019	38	7	0.46	A

20/06/2019	38	8	0.52	A

25/07/2019	37	6	0.39	A

20/08/2019	39	6	0.33	A

### 23

#### UNIT# - MAIN TRAFO UNIT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - PAUWES TRAFO |
| --- | --- |
| DATE MFG | - 2018 |
| MAIN TANK S/N | - 3011160192 |
| KVA | - 60000 |
| PRI | - 157000 V |
| SEC | - 6300 V |
| KILOGRAMS | - 103500 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAF |
| IMPEDENCE | - 13.171% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 30183 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

##### RADIATORS	 - YES FANS	 - YES H2O COOLED	 - NO OIL PUMPS	 - YES TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - YES BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 7. | UAT 3 | PX18-0082 | 22 |

A) Analysis

- Acidity of 0.014mgKOH/g is ACCEPTABLE.

- Dielectric of 78kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 4ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 0.28% M/dw is graded as A. For this transformer, it is recommended to maintain water content in oil at less than 30ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes

11

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	ONLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

21/05/2019	ROUTINE	    0.014 AC	 	85 AC	   0.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.014 AC	37.0 AC	89 AC	   0.5 AC	     	0.8798 AC	CLEAR AC

25/07/2019	ROUTINE	    0.014 AC	 	83 AC	   0.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.014 AC	 	78 AC	   0.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

20/06/2019	4	10251	34223	16	39	232	26	2	ND	87	44793

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

DATE

21/05/2019	35	5	0.35	A

20/06/2019	34	5	0.41	A

25/07/2019	32	5	0.47	A

20/08/2019	35	4	0.28	A

### 22

UNIT# - UAT 3

LOCATION - OUTDOOR OTHER -

#### NAMEPLATE DATA

| MFG | - B & D |
| --- | --- |
| DATE MFG | - 2018 |
| MAIN TANK S/N | - PX18-0082 |
| KVA | - 6300 |
| PRI | - 6300 V |
| SEC | - 6300 V |
| KILOGRAMS | - 52000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - 5.78% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 12000 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

#### RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 8. | TRAFO 1 ESP UNIT 3 | 0073084208 | 11 |

A) Analysis

- Acidity of 0.020mgKOH/g is ACCEPTABLE.

- Dielectric of 69kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water content in oil of 8ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.04% M/dw is graded as B. For this transformer, it is advisable to maintain the water content level below 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

12

OFFLINE

25/08/2018	OFFLINE

25/09/2018	OFFLINE

23/10/2018	ONLINE

22/11/2018	OFFLINE

08/12/2018	OFFLINE

21/05/2019	OFFLINE

20/06/2019	OFFLINE

25/07/2019	OFFLINE

20/08/2019	OFFLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.020 AC	 	53 AC	   0.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.022 AC	 	77 AC	   0.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.020 AC	 	64 AC	   0.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.020 AC	 	63 AC	   0.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.020 AC	 	53 AC	   0.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.020 AC	 	62 AC	   0.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.022 AC	 	85 AC	   0.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.022 AC	35.2 AC	65 AC	   0.5 AC	     	0.8212 QU	CLEAR AC

25/07/2019	ROUTINE	    0.020 AC	 	51 AC	   0.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.020 AC	 	69 AC	   0.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	14	12943	68807	3	62	1243	ND	ND	ND	79	83072

06/12/2017	14	12739	65097	3	66	612	ND	ND	ND	83	78531

28/06/2018	19	15552	64448	3	57	1391	ND	ND	ND	79	81470

20/06/2019	11	19448	64974	6	15	1064	ND	ND	ND	32	85518

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

26	9	1.17	B

26	9	1.17	B

- 10	1.05	B

- 12	1.14	B

- 9	0.86	B

29	9	0.94	B

- 9	1.17	B

- 9	1.17	B

- 9	1.17	B

- 8	1.04	B

### 11

#### UNIT# - TRAFO 1 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0073084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 416 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

##### RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - NO CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 9. | TRAFO 2 ESP UNIT 3 | 0070084208 | 12 |

A) Analysis

- Acidity of 0.028mgKOH/g is ACCEPTABLE.

- Dielectric of 48kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 19ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.80% M/dw is graded as D. For this transformer, it is advisable to maintain the water content level below 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

13

25/08/2018	OFFLINE

25/09/2018	ONLINE

23/10/2018	OFFLINE

22/11/2018	ONLINE

08/12/2018	ONLINE

21/05/2019	OFFLINE

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	OFFLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.022 AC	 	30 AC	   0.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.025 AC	 	67 AC	   0.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.022 AC	 	31 AC	   0.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.025 AC	 	54 AC	   0.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.025 AC	 	33 AC	   0.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.025 AC	 	30 AC	   0.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.028 AC	 	40 AC	   1.0 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.028 AC	31.3 QU	41 AC	   1.0 AC	     	0.8163 QU	CLEAR AC

25/07/2019	ROUTINE	    0.031 AC	 	60 AC	   1.0 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.028 AC	 	48 AC	   1.0 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	38	16781	70523	5	129	2431	3	5	ND	180	89915

06/12/2017	42	19523	66059	3	102	912	ND	ND	ND	147	86641

28/06/2018	43	22272	68719	4	38	1226	ND	ND	ND	85	92302

20/06/2019	13	21221	65168	7	48	1870	ND	ND	ND	68	88327

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

32	25	2.38	D

26	11	1.43	C

39	32	1.76	D 32	13	1.24	B 42	38	1.90	D

43	32	1.44	C

33	18	1.48	C

32	18	1.71	D

29	21	2.20	D

31	19	1.80	D

### 12

#### UNIT# - TRAFO 2 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0070084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 415 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

##### DATE	SERVICE 01/07/2018 PURIFIED

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 10. | TRAFO 3 ESP UNIT 3 | 0072084208 | 13 |

A) Analysis

- Acidity of 0.017mgKOH/g is ACCEPTABLE.

- Dielectric of 32kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water content in oil of 19ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.56% M/dw is graded as C. For this transformer, it is advisable to maintain the water content level below 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

14

25/08/2018	OFFLINE

25/09/2018	ONLINE

23/10/2018	ONLINE

22/11/2018	ONLINE

08/12/2018	ONLINE

21/05/2019	ONLINE

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	ONLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.014 AC	 	43 AC	   0.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.014 AC	 	76 AC	   0.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.020 AC	 	47 AC	   0.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.014 AC	 	49 AC	   0.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.017 AC	 	39 AC	   0.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.014 AC	 	34 AC	   0.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.014 AC	 	41 AC	   0.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.020 AC	38.5 AC	36 AC	   0.5 AC	     	0.8215 QU	CLEAR AC

25/07/2019	ROUTINE	    0.020 AC	 	36 AC	   0.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.017 AC	 	32 AC	   0.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	21	16364	70694	3	38	1068	ND	ND	ND	62	88188

06/12/2017	15	14515	65277	2	40	559	ND	ND	ND	57	80408

28/06/2018	30	15202	64188	4	65	1833	ND	ND	ND	99	81322

20/06/2019	14	18302	64811	6	86	2181	ND	ND	ND	106	85400

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

34	20	1.64	C

25	11	1.43	C 40	20	1.10	B

- 15	0.82	A

- 15	0.82	A

43	18	0.81	A

36	20	1.42	C

35	23	1.63	C

31	20	1.90	D

33	19	1.56	C

### 13

#### UNIT# - TRAFO 3 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

MFG	 - ZHEJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 0072084208

KVA	 -

PRI	 - 72000 V

SEC	 - 415 V

KILOGRAMS	 - 1350

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 731

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

##### DATE	SERVICE 01/07/2018 PURIFIED

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 11. | TRAFO 4 UNIT 3 | 0071084208 | 14 |

A) Analysis

- Acidity of 0.022mgKOH/g is ACCEPTABLE.

- Dielectric of 49kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water content in oil of 11ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.30% M/dw is graded as B. For this transformer, it is advisable to maintain the water content level below 20ppm.

B) Recommendation

- Do carry-out *Liquid Screen, Liquid Power Factor, Inhibitor, Water Content, Metals-In-Oil, Furan Analysis & DGA periodically for Condition Monitoring purposes

15

28/06/2018

24/07/2018	OFFLINE

25/08/2018	OFFLINE

25/09/2018	ONLINE

23/10/2018	OFFLINE

08/12/2018	OFFLINE

21/05/2019	OFFLINE

20/06/2019	OFFLINE

25/07/2019	OFFLINE

20/08/2019	OFFLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.022 AC	 	42 AC	   1.0 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.025 AC	 	66 AC	   1.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.022 AC	 	51 AC	   1.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.022 AC	 	56 AC	   1.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.022 AC	 	44 AC	   1.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.022 AC	 	49 AC	   1.0 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.022 AC	 	58 AC	   1.0 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.022 AC	30.3 QU	51 AC	   1.0 AC	     	0.8451 AC	CLEAR AC

25/07/2019	ROUTINE	    0.020 AC	 	75 AC	   1.0 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.022 AC	 	49 AC	   1.0 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	10	18669	66036	3	24	665	ND	ND	ND	37	85407

06/12/2017	14	15414	63712	2	22	675	ND	ND	ND	38	79839

28/06/2018	20	14690	67822	2	22	683	ND	ND	ND	44	83239

20/06/2019	19	16312	66417	4	37	732	ND	ND	ND	60	83521

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

26	11	1.43	C 27	11	1.30	B

30	11	1.15	B

30	12	1.26	B

30	11	1.15	B 29	13	1.37	C

- 11	1.43	C

- 12	1.42	C

- 11	1.43	C

- 11	1.30

### 14

#### UNIT# - TRAFO 4 UNIT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

MFG	 - ZHEJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 0071084208

KVA	 -

PRI	 - 72000 V

SEC	 - 415 V

KILOGRAMS	 - 1350

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 731

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

##### DATE	SERVICE

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 12. | ASH HANDLING-1 | 10820108 | 15 |

A) Analysis

- Acidity of 0.022mgKOH/g is ACCEPTABLE.

- Dielectric of 30kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 20ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.30% M/dw is graded as B. For this transformer, it is recommended to maintain water content in oil at less than 30ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes

16

28/06/2018

24/07/2018	ONLINE

25/08/2018	OFFLINE

23/10/2018	ONLINE

22/11/2018	ONLINE

08/12/2018	ONLINE

21/05/2019	ONLINE

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	ONLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.022 AC	 	39 AC	   1.0 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.025 AC	 	60 AC	   1.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.025 AC	 	43 AC	   1.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.022 AC	 	28 QU	   1.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.022 AC	 	25 QU	   1.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.022 AC	 	20 UN	   1.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.022 AC	 	28 QU	   1.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.022 AC	36.6 AC	27 QU	   1.5 AC	     	0.8890 AC	CLEAR AC

25/07/2019	ROUTINE	    0.025 AC	 	49 AC	   1.0 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.022 AC	 	30 AC	   1.0 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	35	10984	71058	20	441	5037	7	8	ND	511	87590

06/12/2017	49	12034	67124	20	558	5440	8	8	ND	643	85241

28/06/2018	53	10939	69394	20	557	5425	9	8	ND	647	86405

20/06/2019	53	14032	65585	13	487	5360	ND	11	ND	564	85541

RECOMMENDATION:

GAS LEVELS HAVE REMAINED STABLE. PROCEED WITH ANNUAL MONITORING.

32	20	1.90	B

30	16	1.68	B

35	17	1.21	A 36	29	2.06	C 36	28	1.99	B

35	28	1.99	B 34	29	2.38	C

- 29	2.38	C

- 21	1.49

38	20	1.30

### 15

#### UNIT# - ASH HANDLING-1

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - WOLONG |
| --- | --- |
| DATE MFG | - 2011 |
| MAIN TANK S/N | - 10820108 |
| KVA | - 1600 |
| PRI | - 6300 V |
| SEC | - 400 V |
| KILOGRAMS | - 4505 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - 5.56% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 1023 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

##### DATE	SERVICE

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 13. | ASH HANDLING-2 | 10820107 | 16 |

A) Analysis

- Acidity of 0.025mgKOH/g is ACCEPTABLE.

- Dielectric of 36kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 29ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.88% M/dw is graded as B. For this transformer, it is recommended to maintain water content in oil at less than 30ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

17

22/05/2018	45	GOOD	NONE

28/06/2018	OFFLINE

24/07/2018	ONLINE

25/08/2018	OFFLINE

25/09/2018	OFFLINE

08/12/2018	ONLINE

21/05/2019	OFFLINE

20/06/2019	ONLINE

25/07/2019	ONLINE

20/08/2019	ONLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

24/07/2018	ROUTINE	    0.020 AC	 	27 QU	   1.5 AC	     	 	CLEAR AC

25/08/2018	ROUTINE	    0.022 AC	 	45 AC	   1.5 AC	     	 	CLEAR AC

25/09/2018	ROUTINE	    0.022 AC	 	36 AC	   1.5 AC	     	 	CLEAR AC

23/10/2018	ROUTINE	    0.022 AC	 	36 AC	   1.5 AC	     	 	CLEAR AC

22/11/2018	ROUTINE	    0.022 AC	 	30 AC	   1.5 AC	     	 	CLEAR AC

08/12/2018	ROUTINE	    0.022 AC	 	32 AC	   1.5 AC	     	 	CLEAR AC

21/05/2019	ROUTINE	    0.022 AC	 	32 AC	   1.5 AC	     	 	CLEAR AC

20/06/2019	ROUTINE	    0.022 AC	36.8 AC	37 AC	   1.5 AC	     	0.8889 AC	CLEAR AC

25/07/2019	ROUTINE	    0.025 AC	 	42 AC	   1.5 AC	     	 	CLEAR AC

20/08/2019	ROUTINE	    0.025 AC	 	36 AC	   1.5 AC	     	 	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	18	21157	64224	4	129	1676	ND	1	ND	152	87209

06/12/2017	20	15791	63530	5	275	2783	ND	4	ND	304	82408

28/06/2018	32	22904	67139	4	249	3112	ND	5	ND	290	93445

20/06/2019	39	11205	66397	21	439	5998	11	9	ND	519	84119

RECOMMENDATION:

CARBON MONOXIDE AND CARBON DIOXIDE LEVEL ARE HIGH. OTHER GASES LEVELS ARE ASSESSED AS ACCEPTABLE.

33	30	2.46	C 28	16	1.89	B

30	19	2.00	B

37	23	1.50	B

- 25	1.77	B

- 24	1.56	B

35	23	1.63	B

- 24	1.97	B

- 27	1.92

38	29	1.88

### 16

#### UNIT# - ASH HANDLING-2

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - WOLONG |
| --- | --- |
| DATE MFG | - 2011 |
| MAIN TANK S/N | - 10820107 |
| KVA | - 1600 |
| PRI | - 6300 V |
| SEC | - 400 V |
| KILOGRAMS | - 4505 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - 5.6% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 1023 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - NO CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - NO HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

##### DATE	SERVICE 01/07/2018 PURIFIED

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 14. | TRAFO 1 ESP UNIT 2 | 10037 | 17 |

- Analysis

  - Acidity of 0.034mgKOH/g is ACCEPTABLE.

  - Dielectric of 63kV is ACCEPTABLE.

  - Colour and Visualization of oil is in the ACCEPTABLE range.

  - Water Content in oil of 11ppm is ACCEPTABLE while moisture in solid insulation of 1.15% M/dw is graded as B. For this transformer, it is recommended to maintain the water content less than 20ppm.

- Recommendation

  - Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-In-Oil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

18

| 25/08/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 25/09/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 23/10/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 22/11/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 08/12/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 21/05/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 20/06/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 25/07/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 20/08/2019 | ONLINE |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |
|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
| DATE | SERVICES | ACID | IFT | DIEL | COLOUR |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) | (mN/m) | (kV) |  |  |  |  |  |
| 24/07/2018 | ROUTINE | 0.028 AC |  | 69 AC | 1.0 AC |  |  | CLEAR AC |  |
| 25/08/2018 | ROUTINE | 0.031 AC |  | 74 AC | 1.5 AC |  |  | CLEAR AC |  |
| 25/09/2018 | ROUTINE | 0.028 AC |  | 74 AC | 1.5 AC |  |  | CLEAR AC |  |
| 23/10/2018 | ROUTINE | 0.028 AC |  | 54 AC | 1.5 AC |  |  | CLEAR AC |  |
| 22/11/2018 | ROUTINE | 0.028 AC |  | 54 AC | 1.5 AC |  |  | CLEAR AC |  |
| 08/12/2018 | ROUTINE | 0.028 AC |  | 46 AC | 1.5 AC |  |  | CLEAR AC |  |
| 21/05/2019 | ROUTINE | 0.031 AC |  | 67 AC | 1.5 AC |  |  | CLEAR AC |  |
| 20/06/2019 | ROUTINE | 0.031 AC | 31.0 QU | 62 AC | 1.0 AC |  | 0.8776 AC | CLEAR AC |  |
| 25/07/2019 | ROUTINE | 0.031 AC |  | 64 AC | 1.0 AC |  |  | CLEAR AC |  |
| 20/08/2019 | ROUTINE | 0.034 AC |  | 63 AC | 1.0 AC |  |  | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

28/06/2018	93	17225	43231	5	57	775	ND	2	ND	157	61388

20/06/2019	62	18560	46166	5	50	839	ND	ND	ND	117	65682

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

31	11	1.04	B

    - 12	1.26	B

    - 10	1.05	B

    - 11	1.04	B

    - 10	0.95	B

30	10	1.05	B

30	12	1.26	B 30	13	1.37	C

29	11	1.15

29	11	1.15

### 17

#### UNIT# - TRAFO 1 ESP UNIT 2

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - FUJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 10037 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 380 V |
| KILOGRAMS | - 1000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 630 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

##### RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 15. | TRAFO 2 ESP UNIT 2 | 10036 | 18 |

A) Analysis

- Acidity of 0.065mgKOH/gm is QUESTIONABLE. Although the level remained stable, the oil are containing oxidation by-products. These oxidation by-products are depositing and degrading the oil as well as the paper insulation. Therefore, removal of these contaminations are highly recommended.

- Dielectric of 41kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 12ppm is ACCEPTABLE while moisture in solid insulation of 1.26% M/dw is graded as B. For this transformer, it is recommended to maintain the water content less than 20ppm.

B) Recommendation

- Based on previous oil analysis, the IFT of the oil is unfavorable, it is recommended to perform Transformer Oil Regeneration on this unit. Transformer oil regeneration at this stage of contamination will effectively remove unwanted oxidation byproducts from the insulating oil. This process will restore the oil back to its original quality, thus protecting the paper insulation and extending the transformer serviceable lifespan. Furthermore, oil inhibitor 2,6-DBPC and passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

19

| 25/08/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 25/09/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 23/10/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 22/11/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 08/12/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 21/05/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 20/06/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 25/07/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 20/08/2019 | ONLINE |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |
|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
| DATE | SERVICES | ACID | IFT | DIEL | COLOUR |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) | (mN/m) | (kV) |  |  |  |  |  |
| 24/07/2018 | ROUTINE | 0.059 QU |  | 79 AC | 1.5 AC |  |  | CLEAR AC |  |
| 25/08/2018 | ROUTINE | 0.062 QU |  | 67 AC | 1.5 AC |  |  | CLEAR AC |  |
| 25/09/2018 | ROUTINE | 0.056 QU |  | 51 AC | 1.5 AC |  |  | CLEAR AC |  |
| 23/10/2018 | ROUTINE | 0.062 QU |  | 67 AC | 1.5 AC |  |  | CLEAR AC |  |
| 22/11/2018 | ROUTINE | 0.062 QU |  | 61 AC | 1.5 AC |  |  | CLEAR AC |  |
| 08/12/2018 | ROUTINE | 0.062 QU |  | 59 AC | 1.5 AC |  |  | CLEAR AC |  |
| 21/05/2019 | ROUTINE | 0.065 QU |  | 77 AC | 1.0 AC |  |  | CLEAR AC |  |
| 20/06/2019 | ROUTINE | 0.065 QU | 29.7 QU | 76 AC | 1.0 AC |  | 0.8655 AC | CLEAR AC |  |
| 25/07/2019 | ROUTINE | 0.062 QU |  | 47 AC | 1.5 AC |  |  | CLEAR AC |  |
| 20/08/2019 | ROUTINE | 0.065 QU |  | 41 AC | 1.5 AC |  |  | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

28/06/2018	8	22714	64906	5	67	879	ND	ND	ND	80	88579

20/06/2019	5	29439	65338	5	25	977	ND	ND	ND	35	95789

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

31	8	0.76	A

31	10	0.95	B

- 9	0.94	B

31	13	1.24	B

33	8	0.66	A

- 8	0.84	A

- 11	1.15	B

- 12	1.14	B

28	11	1.30

30	12	1.26

### 18

#### UNIT# - TRAFO 2 ESP UNIT 2

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - FUJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 10036 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 380 V |
| KILOGRAMS | - 1000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 630 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

##### RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 16. | TRAFO 3 ESP UNIT 2 | 10033 | 19 |

A) Analysis

- Acidity of 0.067mgKOH/g is QUESTIONABLE. Although the level remained stable, the oil are containing oxidation by-products. These oxidation byproducts are depositing and degrading the oil as well as the paper insulation. Therefore, removal of these contaminations are highly recommended.

- Dielectric of 58kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 14ppm is ACCEPTABLE while moisture in solid insulation of 1.33% M/dw is graded as B. For this transformer, it is recommended to maintain the water content less than 20ppm.

B) Recommendation

- Based on previous oil analysis, the IFT of the oil is unfavorable. It is recommended to perform Transformer Oil Regeneration on this unit. Transformer oil regeneration at this stage of contamination will effectively remove unwanted oxidation byproducts from the insulating oil. This process will restore the oil back to its original quality, thus protecting the paper insulation and extending the transformer serviceable lifespan. Furthermore, oil inhibitor 2,6-DBPC and passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

20

| 25/08/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 25/09/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 23/10/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 22/11/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 08/12/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 21/05/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 20/06/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 25/07/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 20/08/2019 | ONLINE |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |
|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
| DATE | SERVICES | ACID | IFT | DIEL | COLOUR |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) | (mN/m) | (kV) |  |  |  |  |  |
| 24/07/2018 | ROUTINE | 0.070 QU |  | 67 AC | 1.5 AC |  |  | CLEAR AC |  |
| 25/08/2018 | ROUTINE | 0.067 QU |  | 73 AC | 1.5 AC |  |  | CLEAR AC |  |
| 25/09/2018 | ROUTINE | 0.067 QU |  | 59 AC | 1.5 AC |  |  | CLEAR AC |  |
| 23/10/2018 | ROUTINE | 0.070 QU |  | 86 AC | 1.5 AC |  |  | CLEAR AC |  |
| 22/11/2018 | ROUTINE | 0.070 QU |  | 13 UN | 1.5 AC |  |  | CLEAR AC |  |
| 08/12/2018 | ROUTINE | 0.070 QU |  | 8 UN | 1.5 AC |  |  | CLEAR AC |  |
| 21/05/2019 | ROUTINE | 0.073 QU |  | 50 AC | 1.5 AC |  |  | CLEAR AC |  |
| 20/06/2019 | ROUTINE | 0.073 QU | 26.5 UN | 53 AC | 1.5 AC |  | 0.8687 AC | CLEAR AC |  |
| 25/07/2019 | ROUTINE | 0.070 QU |  | 48 AC | 1.5 AC |  |  | CLEAR AC |  |
| 20/08/2019 | ROUTINE | 0.067 QU |  | 58 AC | 1.5 AC |  |  | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

28/06/2018	14	17627	48672	4	47	935	ND	ND	ND	65	67299

20/06/2019	16	17449	51923	5	58	1049	ND	ND	ND	79	70500

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

32	12	1.14	B 30	13	1.37	C 30	12	1.26	B

- 13	1.24	B

- 84	6.89	E

31	84	7.98	E 30	13	1.37	C

- 13	1.37	C

29	13	1.37	C

- 14	1.33

### 19

#### UNIT# - TRAFO 3 ESP UNIT 2

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - FUJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 10033 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 380 V |
| KILOGRAMS | - 1000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 630 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

##### RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 17. | TRAFO 4 ESP UNIT 2 | 10032 | 20 |

A) Analysis

- Acidity of 0.036mgKOH/g is ACCEPTABLE.

- Dielectric of 45kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 12ppm is ACCEPTABLE while moisture in solid insulation of 1.14% M/dw is graded as B. For this transformer, it is recommended to maintain the water content less than 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

21

| 28/06/2018 | ONLINE |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 24/07/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 25/08/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 23/10/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 22/11/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 08/12/2018 | OFFLINE |  |  |  |  |  |  |  |  |
| 21/05/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 20/06/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 25/07/2019 | OFFLINE |  |  |  |  |  |  |  |  |
| 20/08/2019 | ONLINE |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |
|  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
| DATE | SERVICES | ACID | IFT | DIEL | COLOUR |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) | (mN/m) | (kV) |  |  |  |  |  |
| 24/07/2018 | ROUTINE | 0.031 AC |  | 59 AC | 1.0 AC |  |  | CLEAR AC |  |
| 25/08/2018 | ROUTINE | 0.031 AC |  | 68 AC | 1.5 AC |  |  | CLEAR AC |  |
| 25/09/2018 | ROUTINE | 0.031 AC |  | 51 AC | 1.5 AC |  |  | CLEAR AC |  |
| 23/10/2018 | ROUTINE | 0.034 AC |  | 57 AC | 1.0 AC |  |  | CLEAR AC |  |
| 22/11/2018 | ROUTINE | 0.034 AC |  | 69 AC | 1.0 AC |  |  | CLEAR AC |  |
| 08/12/2018 | ROUTINE | 0.034 AC |  | 61 AC | 1.5 AC |  |  | CLEAR AC |  |
| 21/05/2019 | ROUTINE | 0.036 AC |  | 60 AC | 1.0 AC |  |  | CLEAR AC |  |
| 20/06/2019 | ROUTINE | 0.036 AC | 30.3 QU | 61 AC | 1.0 AC |  | 0.8732 AC | CLEAR AC |  |
| 25/07/2019 | ROUTINE | 0.034 AC |  | 59 AC | 1.0 AC |  |  | CLEAR AC |  |
| 20/08/2019 | ROUTINE | 0.036 AC |  | 45 AC | 1.5 AC |  |  | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

28/06/2018	22	25201	74464	5	85	823	ND	ND	ND	112	100600 20/06/2019	33	25208	70145	4	35	853	ND	ND	ND	72	96278

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

32	13	1.24	B

- 10	0.95	B

29	11	1.15	B 32	15	1.42	C 33	14	1.15	B 31	18	1.71	D 31	14	1.33	B 30	14	1.47	C 29	12	1.26	B

- 12	1.14

### 20

#### UNIT# - TRAFO 4 ESP UNIT 2

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - FUJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 10032 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 380 V |
| KILOGRAMS | - 1000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 630 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

##### RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 18. | MAIN TRAFO UNIT 2 | 1006902 | 21 |

A) Analysis

- Acidity of 0.014mgKOH/g is ACCEPTABLE.

- Dielectric of 36kV is ACCEPTABLE.

- Colour and Visualization of oil is in the ACCEPTABLE range.

- Water Content in oil of 8ppm is ACCEPTABLE while moisture in solid insulation of 0.66% M/dw is graded as A. For this transformer, it is recommended to maintain the water content less than 20ppm.

B) Recommendation

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes.

22

| 28/06/2018 | OFFLINE | 50 | 45 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 24/07/2018 | ONLINE |  |  | GOOD |  |  |  |  |  |  |
| 25/08/2018 | ONLINE |  |  |  |  |  |  |  |  |  |
| 25/09/2018 | ONLINE |  |  |  |  |  |  |  |  |  |
| 23/10/2018 | OFFLINE |  |  |  |  |  |  |  |  |  |
| 08/12/2018 | OFFLINE |  |  |  |  |  |  |  |  |  |
| 21/05/2019 | ONLINE |  |  |  |  |  |  |  |  |  |
| 20/06/2019 | ONLINE |  |  |  |  |  |  |  |  |  |
| 25/07/2019 | ONLINE |  |  |  |  |  |  |  |  |  |
| 20/08/2019 | ONLINE |  |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |
|  |  | ASTM D974 |  | ASTM D971 | IEC 156 | ASTM D1500 |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
| DATE | SERVICES | ACID |  | IFT | DIEL | COLOUR |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) | (kV) |  |  |  |  |  |
| 24/07/2018 | ROUTINE | 0.011 AC |  |  | 79 AC | 0.5 AC |  |  | CLEAR AC |  |
| 25/08/2018 | ROUTINE | 0.011 AC |  |  | 83 AC | 0.5 AC |  |  | CLEAR AC |  |
| 25/09/2018 | ROUTINE | 0.011 AC |  |  | 90 AC | 0.5 AC |  |  | CLEAR AC |  |
| 23/10/2018 | ROUTINE | 0.011 AC |  |  | 64 AC | 0.5 AC |  |  | CLEAR AC |  |
| 22/11/2018 | ROUTINE | 0.011 AC |  |  | 61 AC | 0.5 AC |  |  | CLEAR AC |  |
| 08/12/2018 | ROUTINE | 0.011 AC |  |  | 57 AC | 0.5 AC |  |  | CLEAR AC |  |
| 21/05/2019 | ROUTINE | 0.011 AC |  |  | 63 AC | 0.5 AC |  |  | CLEAR AC |  |
| 20/06/2019 | ROUTINE | 0.011 AC |  | 39.3 AC | 58 AC | 0.5 AC |  | 0.8745 AC | CLEAR AC |  |
| 25/07/2019 | ROUTINE | 0.011 AC |  |  | 49 AC | 0.5 AC |  |  | CLEAR AC |  |
| 20/08/2019 | ROUTINE | 0.014 AC |  |  | 36 AC | 0.5 AC |  |  | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612C), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

28/06/2018	19	12733	53386	10	193	2448	ND	2	ND	224	68791

20/06/2019	10	17382	50681	8	107	712	ND	2	ND	127	68902

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

- 11	0.90	B

- 9	0.74	A

32	7	0.67	A

29	7	0.74	A

32	7	0.67	A

30	6	0.63	A

- 7	0.50	A

35	11	0.78	A

32	7	0.67	A

34	8	0.66	A

### 21

#### UNIT# - MAIN TRAFO UNIT 2

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - WOLONG |
| --- | --- |
| DATE MFG | - 2011 |
| MAIN TANK S/N | - 1006902 |
| KVA | - 33000 |
| PRI | - 170000 V |
| SEC | - 6300 V |
| KILOGRAMS | - 81000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - OFAF |
| IMPEDENCE | - 13.03% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 30857 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

##### RADIATORS	 - YES FANS	 - YES H2O COOLED	 - NO OIL PUMPS	 - YES TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - YES BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

3.0 	Summary of Our Comments & Recommendations:

| No. | Sub Name | Unit No. | TC | Recommendation |
| --- | --- | --- | --- | --- |
| 1. | MAIN TRAFO UNIT 1 | 100691 | 4 |  Periodic condition monitoring |
| 2. | TRAFO 1 ESP UNIT 1 | 10937 | 5 |  Periodic condition monitoring |
| 3. | TRAFO 2 ESP UNIT 1 | 10035 | 6 |  Perform OIL REGENERATION |
| 4. | TRAFO 3 ESP UNIT 1 | 10031 | 7 |  Perform OIL REGENERATION |
| 5. | TRAFO 4 ESP UNIT 1 | 10034 | 8 |  Periodic condition monitoring |
| 6. | MAIN TRAFO UNIT 3 | 3011160192 | 23 |  Periodic condition monitoring |
| 7. | UAT 3 | PX18-0082 | 22 |  Periodic condition monitoring |
| 8. | TRAFO 1 ESP UNIT 3 | 0073084208 | 11 |  Periodic condition monitoring |
| 9. | TRAFO 2 ESP UNIT 3 | 0070084208 | 12 |  Periodic condition monitoring |
| 10. | TRAFO 3 ESP UNIT 3 | 0072084208 | 13 |  Periodic condition monitoring |
| 11. | TRAFO 4 UNIT 3 | 0071084208 | 14 |  Periodic condition monitoring |
| 12. | ASH HANDLING-1 | 10820108 | 15 |  Periodic condition monitoring |
| 13. | ASH HANDLING-2 | 10820107 | 16 |  Periodic condition monitoring |
| 14. | TRAFO 1 ESP UNIT 2 | 10037 | 17 |  Periodic condition monitoring |
| 15. | TRAFO 2 ESP UNIT 2 | 10036 | 18 |  Perform OIL REGENERATION |
| 16. | TRAFO 3 ESP UNIT 2 | 10033 | 19 |  Perform OIL RE GENERATION |

23

Ref No : TXM/MKT-1200/SA/CI19034

| No. | Sub Name | Unit No. | TC | Recommendation |
| --- | --- | --- | --- | --- |
| 17. | TRAFO 4 ESP UNIT 2 | 10032 | 20 |  Periodic condition monitoring |
| 18. | MAIN TRAFO UNIT 2 | 1006902 | 21 |  Periodic condition monitoring |

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 24 of 24

|  | no | Test Cer. | Date Test | nama unit |  | Serial number | thn opr | Jumlah minyak, liter | Buatan | hasil test laboratorium |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | acid | ift | diel. | color | spec. Graf. | visual | sedi. | moisture |  | dga ASTM D3612 |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ppm | grade | H2 | O2 | N2 | CH4 | CO | CO2 |
|  | Standard yang dipakai |  |  |  |  |  |  |  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | ASTM D1533 |  | hydrogen | oksigen | nitrogen | methane | carbon monoksida | carbon dioksida |
|  |  | BATASAN OPERASI |  |  |  |  |  |  |  | < 0,06 | > 32 | > 30 | < 3,5 | > 0,84 | C |  | < 20 |  | < 100 |  |  | < 120 | < 350 | < 2.500 |
|  |  | 4 | 21/05/2018 |  |  |  |  |  |  | 0,011 |  | 77 | 0,5 |  | C |  | 10 | B |  |  |  |  |  |  |
|  |  | 4 | 28/06/2018 |  |  |  |  |  |  | 0,014 | 41,9 | 69 | 0,5 | 0,8716 | C |  | 7 | A | 176 | 11.044 | 46.776 | 41 | 758 | 3.393 |
|  |  | 4 | 24/07/2018 |  |  |  |  |  |  | 0,014 |  | 86 | 0,5 |  | C |  | 6 | A |  |  |  |  |  |  |
|  |  | 4 | 25/08/2018 |  |  |  |  |  |  | 0,017 |  | 90 | 0,5 |  | C |  | 6 | A |  |  |  |  |  |  |
|  |  | 4 | 25/09/2018 |  |  |  |  |  |  | 0,014 |  | 96 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 4 | 23/10/2018 |  |  |  |  |  |  | 0,014 |  | 83 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 4 | 22/11/2018 |  |  |  |  |  |  | 0,014 |  | 73 | 0,5 |  | C |  | 9 | A |  |  |  |  |  |  |
|  |  | 4 | 08/12/2018 |  |  |  |  |  |  | 0,014 |  | 75 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 4 | 21/05/2019 |  |  |  |  |  |  | 0,014 |  | 71 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 4 | 20/06/2019 |  |  |  |  |  |  | 0,017 | 41,3 | 66 | 0,5 | 0,8789 | C |  | 7 | A |  | 19.122 | 60.738 | 26 | 756 | 3.272 |
|  |  | 4 | 25/07/2019 |  |  |  |  |  |  | 0,014 |  | 79 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 4 | 20/08/2019 |  |  |  |  |  |  | 0,014 |  | 61 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  | 2 | 5 | 21/05/2018 | Trafo 1 ESP | 1 | 10937 | 2010 | 1.143 | Fujia | 0,065 |  | 38 | 1,5 |  | C |  | 33 | E |  |  |  |  |  |  |
|  |  | 5 | 28/06/2018 |  |  |  |  |  |  | 0,067 | 25,9 | 32 | 1,5 | 0,8560 | C |  | 30 | E | 44 | 20.039 | 64.529 | 4 | 119 | 1.696 |
|  |  | 5 | 24/07/2018 |  |  |  |  |  |  | 0,073 |  | 38 | 1,5 |  | C |  | 19 | D |  |  |  |  |  |  |
|  |  | 5 | 25/08/2018 |  |  |  |  |  |  | 0,020 |  | 71 | 0,5 |  | C |  | 12 | B |  |  |  |  |  |  |
|  |  | 5 | 25/09/2018 |  |  |  |  |  |  | 0,017 |  | 63 | 0,5 |  | C |  | 18 | B |  |  |  |  |  |  |
|  |  | 5 | 23/10/2018 |  |  |  |  |  |  | 0,020 |  | 49 | 0,5 |  | C |  | 24 | B |  |  |  |  |  |  |
|  |  | 5 | 22/11/2018 |  |  |  |  |  |  | 0,017 |  | 30 | 0,5 |  | C |  | 23 | C |  |  |  |  |  |  |
|  |  | 5 | 08/12/2018 |  |  |  |  |  |  | 0,017 |  | 41 | 0,5 |  | C |  | 18 | D |  |  |  |  |  |  |
|  |  | 5 | 21/05/2019 |  |  |  |  |  |  | 0,017 |  | 40 | 0,5 |  | C |  | 22 | C |  |  |  |  |  |  |
|  |  | 5 | 20/06/2019 |  |  |  |  |  |  | 0,017 | 38,7 | 34 | 0,5 | 0,8747 | C |  | 23 | C | 22 | 27.043 | 68.613 | 5 |  | 689 |
|  |  | 5 | 25/07/2019 |  |  |  |  |  |  | 0,017 |  | 61 | 0,5 |  | C |  | 18 | D |  |  |  |  |  |  |
|  |  | 5 | 20/08/2019 |  |  |  |  |  |  | 0,017 |  | 56 | 0,5 |  | C |  | 16 | C |  |  |  |  |  |  |
|  | 3 | 6 | 21/05/2018 | Trafo 2 ESP | 1 | 10035 | 2010 | 1.143 | Fujia | 0,056 |  | 45 | 1,5 |  | C |  | 20 | D |  |  |  |  |  |  |
|  |  | 6 | 28/06/2018 |  |  |  |  |  |  | 0,059 | 27,6 | 55 | 1,5 | 0,8570 | C |  | 17 | C | 22 | 22.494 | 64.443 | 4 | 57 | 789 |
|  |  | 6 | 24/07/2018 |  |  |  |  |  |  | 0,062 |  | 47 | 1,5 |  | C |  | 15 | C |  |  |  |  |  |  |
|  |  | 6 | 25/08/2018 |  |  |  |  |  |  | 0,022 |  | 56 | 0,5 |  | C |  | 13 | B |  |  |  |  |  |  |
|  |  | 6 | 25/09/2018 |  |  |  |  |  |  | 0,020 |  | 67 | 0,5 |  | C |  | 11 | B |  |  |  |  |  |  |
|  |  | 6 | 23/10/2018 |  |  |  |  |  |  | 0,020 |  | 71 | 0,5 |  | C |  | 14 | B |  |  |  |  |  |  |
|  |  | 6 | 22/11/2018 |  |  |  |  |  |  | 0,020 |  | 63 | 0,5 |  | C |  | 18 | C |  |  |  |  |  |  |
|  |  | 6 | 08/12/2018 |  |  |  |  |  |  | 0,020 |  | 51 | 0,5 |  | C |  | 14 | B |  |  |  |  |  |  |
|  |  | 6 | 21/05/2019 |  |  |  |  |  |  | 0,020 |  | 71 | 0,5 |  | C |  | 15 | B |  |  |  |  |  |  |
|  |  | 6 | 20/06/2019 |  |  |  |  |  |  | 0,020 | 27,9 | 68 | 0,5 | 0,8658 | C |  | 17 | B | 23 | 17.710 | 61.707 | 5 | 23 | 842 |
|  |  | 6 | 25/07/2019 |  |  |  |  |  |  | 0,022 |  | 67 | 0,5 |  | C |  | 15 | C |  |  |  |  |  |  |
|  |  | 6 | 20/08/2019 |  |  |  |  |  |  | 0,020 |  | 51 | 0,5 |  | C |  | 15 | C |  |  |  |  |  |  |
|  | 4 | 7 | 21/05/2018 | Trafo 3 ESP | 1 | 10031 | 2010 | 1.143 | Fujia | 0,056 |  | 48 | 1,5 |  | C |  | 21 | D |  |  |  |  |  |  |
|  |  | 7 | 28/06/2018 |  |  |  |  |  |  | 0,053 | 29,7 | 62 | 1,5 | 0,8605 | C |  | 17 | D | 9 | 17.958 | 66.007 | 4 | 46 | 781 |
|  |  | 7 | 24/07/2018 |  |  |  |  |  |  | 0,510 |  | 64 | 1,5 |  | C |  | 17 | D |  |  |  |  |  |  |
|  |  | 7 | 25/08/2018 |  |  |  |  |  |  | 0,056 |  | 57 | 1,5 |  | C |  | 15 | C |  |  |  |  |  |  |
|  |  | 7 | 25/09/2018 |  |  |  |  |  |  | 0,051 |  | 46 | 1,5 |  | C |  | 21 | D |  |  |  |  |  |  |
|  |  | 7 | 23/10/2018 |  |  |  |  |  |  | 0,056 |  | 44 | 1,5 |  | C |  | 20 | C |  |  |  |  |  |  |
|  |  | 7 | 22/11/2018 |  |  |  |  |  |  | 0,056 |  | 39 | 1,5 |  | C |  | 22 | C |  |  |  |  |  |  |
|  |  | 7 | 08/12/2018 |  |  |  |  |  |  | 0,056 |  | 39 | 1,5 |  | C |  | 20 | C |  |  |  |  |  |  |
|  |  | 7 | 21/05/2019 |  |  |  |  |  |  | 0,051 |  | 33 | 1,5 |  | C |  | 19 | B |  |  |  |  |  |  |
|  |  | 7 | 20/06/2019 |  |  |  |  |  |  | 0,051 | 29,6 | 30 | 1,5 | 0,8689 | C |  | 19 | B | 16 | 17.771 | 65.478 | 6 | 73 | 829 |
|  |  | 7 | 25/07/2019 |  |  |  |  |  |  | 0,056 |  | 48 | 1,5 |  | C |  | 15 | C |  |  |  |  |  |  |
|  |  | 7 | 20/08/2019 |  |  |  |  |  |  | 0,051 |  | 43 | 1,5 |  | C |  | 18 | D |  |  |  |  |  |  |
|  | 5 | 8 | 21/05/2018 | Trafo 4 ESP | 1 | 10034 | 2010 | 1.143 | Fujia | 0,034 |  | 37 | 1,5 |  | C |  | 23 | D |  |  |  |  |  |  |
|  |  | 8 | 28/06/2018 |  |  |  |  |  |  | 0,037 | 27,5 | 55 | 1,5 | 0,8653 | C |  | 20 | D | 9 | 17.962 | 64.248 | 4 | 75 | 1.054 |
|  |  | 8 | 24/07/2018 |  |  |  |  |  |  | 0,039 |  | 50 | 1,5 |  | C |  | 19 | D |  |  |  |  |  |  |
|  |  | 8 | 25/08/2018 |  |  |  |  |  |  | 0,017 |  | 61 | 0,5 |  | C |  | 14 | C |  |  |  |  |  |  |
|  |  | 8 | 25/09/2018 |  |  |  |  |  |  | 0,014 |  | 45 | 0,5 |  | C |  | 20 | D |  |  |  |  |  |  |

|  | no | Test Cer. | Date Test | m cennix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MALAYSIAN LAB RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | nama unit |  |  |  |  |  | lpf (C) |  | dbpc | furan |  | metal in oil |  |  | corr. sul | keterangan |  |
|  |  |  |  |  |  | C2H6 | C2H4 | C2H2 | TOT | 25O | 100O |  |  | Al |  | Fe | Cu |  |  |  |
|  | Standa |  |  |  |  | r ethane | ethylene | acethylene |  | ASTM D924 |  | ASTM D2668 | ASTM D5837 |  | ASTM D3635 |  |  | ASTM D1275B |  |  |
|  |  |  |  |  |  | < 65 | <50 | < 2 | < 687 | < 0.1 | < 2.9 | > .2 | < 100 | 0,00 |  | 0,00 | 0,00 |  | Non corrosive |  |
|  |  | 4 | 21/05/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 28/06/2018 |  |  | 5 | 6 | 0 | 986 | 0,000 | 0,140 | 0,24 | 0 | 0,00 |  | 0,00 | 0,04 | 3 A | Suspec Corrosive | Add passivator |
|  |  | 4 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 20/06/2019 |  |  | 2 | 3 | 0 | 805 | 0,000 | 0,180 | 0,24 | 0 | 0,01 |  | 0,00 | 0,02 | 3A | Suspec Corrosive | Add passivator |
|  |  | 4 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 4 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 2 | 5 | 21/05/2018 | Trafo 1 ESP | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 5 | 28/06/2018 |  |  | 0 | 2 | 0 | 169 | 0,000 | 0,680 | 0,00 | 85 | 0,00 |  | 0,00 | 0,03 | 1 B | Non corrosive | Perform OIL REGENERATION |
|  |  | 5 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 5 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring (change oil on beginning of August 2018 |
|  |  | 5 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 5 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 5 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Preparing for Purification |
|  |  | 5 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Preparing for Purification |
|  |  | 5 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Preparing for Purification |
|  |  | 5 | 20/06/2019 |  |  | 0 | 0 | 0 | 63 | 0,000 | 0,230 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 | 1B | Non corrosive | Preparing for Purification |
|  |  | 5 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Preparing for Purification |
|  |  | 5 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 3 | 6 | 21/05/2018 | Trafo 2 ESP | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 6 | 28/06/2018 |  |  | 0 | 0 | 0 | 83 | 0,000 | 1,130 | 0,00 | 84 | 0,00 |  | 0,00 | 0,02 | 1 B | Non corrosive | Perform OIL REGENERATION |
|  |  | 6 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 6 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring (change oil on beginning of August 2018 |
|  |  | 6 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 6 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 6 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 6 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 6 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 6 | 20/06/2019 |  |  | 0 | 0 | 0 | 51 | 0,000 | 0,680 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 | 2E | Non corrosive | Perform OIL REGENERATION Perform OIL REGENERATION |
|  |  | 6 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 6 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  | 4 | 7 | 21/05/2018 | Trafo 3 ESP | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Retest 6 months: Acidity, IFT, Dielectric and Water Content Add inhibitor 2,6-DBPC and PASSIVATOR Periodic condition monitoring Periodic condition monitoring Perform OIL REGENERATION Perform OIL REGENERATION Perform OIL REGENERATION Perform OIL REGENERATION Perform OIL REGENERATION Perform OIL REGENERATION Perform OIL REGENERATION |
|  |  | 7 | 28/06/2018 |  |  | 0 | 1 | 0 | 60 | 0,000 | 1,030 | 0,00 | 20 | 0,00 |  | 0,00 | 0,11 | 1 B | Non corrosive |  |
|  |  | 7 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 | 20/06/2019 |  |  | 0 | 1 | 0 | 96 | 0,000 | 0,520 | 0,00 | 57 | 0,01 |  | 0,00 | 0,02 | 2E | Non corrosive |  |
|  |  | 7 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 7 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  | 5 | 8 | 21/05/2018 | Trafo 4 ESP | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 8 | 28/06/2018 |  |  | 0 | 2 | 0 | 90 | 0,060 | 2,850 | 0,02 | 21 | 0,00 |  | 0,00 | 0,05 | 3 A | Suspec Corrosive | Perform OIL REGENERATION |
|  |  | 8 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 8 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring (change oil on beginning of August 2018 |
|  |  | 8 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFICATION |

|  | no | Test Cer. | Date Test | nama unit |  | r | PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Standa |  |  |  |  |  |  |
|  |  |  |  |  |  |  | For Test 25 JuIy 2019 Kondisi trafro masih seperti bulan yang lalu Kami tetap meyarankan untuk ESP 1 Unit 1 dan ESP 2 dan 3 Unit 3 dilakukan PURIFIKASI dengan temperatur sekitar 700 GANTI MINYAK pada trafo ESP 3 Unit 1 dan ESP 2 dan 3 Unit 2 For Test 25 JuIy 2019 Trend penurunan kondisi trafo ESP Jadi kami sarankan untuk ESP 1 Unit 1 dan ESP 2 dan 3 Unit 3 segera dilakukan PURIFIKASI dengan temperatur sekitar 700 GANTI MINYAK pada trafo ESP 3 Unit 1 dan ESP 2 dan 3 Unit 2 For Test 20 Juni 2019 Ada penurunan kondisi trafo ESP terutama Unit 1 dan 2 Jadi kami sarankan untuk ESP 1 Unit 1 dan Ash Handling 1 segera dilakukan PURIFIKASI dengan temperatur sekitar 700 GANTI MINYAK pada trafo ESP 3 Unit 1 dan ESP 2 dan 3 Unit 2 Monitoring kuaIitas minyak untuk ESP 1 dan 4 Unit 2 For TEST 21 Mei 2019 Ada beberapa perubahan kondisi trafo seperti, Main Trafo dan UAT Unit 3 yang ganti Trafo baru serta perbaikan oIi diESP 3 Unit 2 Jadi kami sarankan untuk ESP 1 dan 4 Unit 1, ESP 2 Unit 3 dan Ash Handling 1 segera dilakukan PURIFIKASI dengan temperatur sekitar 700 GANTI MINYAK pada trafo ESP 3 Unit 1 dan ESP 2 dan 3 Unit 2 For TEST 08 Desember 2018 Pada dasarnya kondisi masih sama dengan pada saat pengetesan bulan November 2018, Untuk trafo ESP 3 Unit 2 kondisi BDV sudah sangat rendah sekali, harap menjadikan perhatian khusus Kami sarankan untuk Untuk ESP 1 dan 4 Unit 1, ESP 2 Unit 3 dan Ash Handling 1 segera dilakukan PURIFIKASI dengan temperatur sekitar 700 |
|  |  | 4 | 21/05/2018 |  |  |  |  |
|  |  | 4 | 28/06/2018 |  |  |  |  |
|  |  | 4 | 24/07/2018 |  |  |  |  |
|  |  | 4 | 25/08/2018 |  |  |  |  |
|  |  | 4 | 25/09/2018 |  |  |  |  |
|  |  | 4 | 23/10/2018 |  |  |  |  |
|  |  | 4 | 22/11/2018 |  |  |  |  |
|  |  | 4 | 08/12/2018 |  |  |  |  |
|  |  | 4 | 21/05/2019 |  |  |  |  |
|  |  | 4 | 20/06/2019 |  |  |  |  |
|  |  | 4 | 25/07/2019 |  |  |  |  |
|  |  | 4 | 20/08/2019 |  |  |  |  |
|  | 2 | 5 | 21/05/2018 | Trafo 1 ESP | 1 |  |  |
|  |  | 5 | 28/06/2018 |  |  |  |  |
|  |  | 5 | 24/07/2018 |  |  |  |  |
|  |  | 5 | 25/08/2018 |  |  |  |  |
|  |  | 5 | 25/09/2018 |  |  |  |  |
|  |  | 5 | 23/10/2018 |  |  |  |  |
|  |  | 5 | 22/11/2018 |  |  |  |  |
|  |  | 5 | 08/12/2018 |  |  |  |  |
|  |  | 5 | 21/05/2019 |  |  |  |  |
|  |  | 5 | 20/06/2019 |  |  |  |  |
|  |  | 5 | 25/07/2019 |  |  |  |  |
|  |  | 5 | 20/08/2019 |  |  |  |  |
|  | 3 | 6 | 21/05/2018 | Trafo 2 ESP | 1 |  |  |
|  |  | 6 | 28/06/2018 |  |  |  |  |
|  |  | 6 | 24/07/2018 |  |  |  |  |
|  |  | 6 | 25/08/2018 |  |  |  |  |
|  |  | 6 | 25/09/2018 |  |  |  |  |
|  |  | 6 | 23/10/2018 |  |  |  |  |
|  |  | 6 | 22/11/2018 |  |  |  |  |
|  |  | 6 | 08/12/2018 |  |  |  |  |
|  |  | 6 | 21/05/2019 |  |  |  |  |
|  |  | 6 | 20/06/2019 |  |  |  |  |
|  |  | 6 | 25/07/2019 |  |  |  |  |
|  |  | 6 | 20/08/2019 |  |  |  |  |
|  | 4 | 7 | 21/05/2018 | Trafo 3 ESP | 1 |  |  |
|  |  | 7 | 28/06/2018 |  |  |  |  |
|  |  | 7 | 24/07/2018 |  |  |  |  |
|  |  | 7 | 25/08/2018 |  |  |  |  |
|  |  | 7 | 25/09/2018 |  |  |  |  |
|  |  | 7 | 23/10/2018 |  |  |  |  |
|  |  | 7 | 22/11/2018 |  |  |  |  |
|  |  | 7 | 08/12/2018 |  |  |  |  |
|  |  | 7 | 21/05/2019 |  |  |  |  |
|  |  | 7 | 20/06/2019 |  |  |  |  |
|  |  | 7 | 25/07/2019 |  |  |  |  |
|  |  | 7 | 20/08/2019 |  |  |  |  |
|  | 5 | 8 | 21/05/2018 | Trafo 4 ESP | 1 |  |  |
|  |  | 8 | 28/06/2018 |  |  |  |  |
|  |  | 8 | 24/07/2018 |  |  |  |  |
|  |  | 8 | 25/08/2018 |  |  |  |  |
|  |  | 8 | 25/09/2018 |  |  |  |  |

|  | no | Test Cer. | Date Test | nama unit |  | Serial number | thn opr | Jumlah minyak, liter | Buatan | hasil test laboratorium |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | acid | ift | diel. | color | spec. Graf. | visual | sedi. | moisture |  | dga ASTM D3612 |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ppm | grade | H2 | O2 | N2 | CH4 | CO | CO2 |
|  | Standard yang dipakai |  |  |  |  |  |  |  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | ASTM D1533 |  | hydrogen | oksigen | nitrogen | methane | carbon monoksida | carbon dioksida |
|  |  | BATASAN OPERASI |  |  |  |  |  |  |  | < 0,06 | > 32 | > 30 | < 3,5 | > 0,84 | C |  | < 20 |  | < 100 |  |  | < 120 | < 350 | < 2.500 |
|  |  | 8 | 23/10/2018 |  |  |  |  |  |  | 0,014 |  | 52 | 0,5 |  | C |  | 21 | B |  |  |  |  |  |  |
|  |  | 8 | 22/11/2018 |  |  |  |  |  |  | 0,014 |  | 44 | 0,5 |  | C |  | 21 | C |  |  |  |  |  |  |
|  |  | 8 | 08/12/2018 |  |  |  |  |  |  | 0,014 |  | 47 | 0,5 |  | C |  | 20 | B |  |  |  |  |  |  |
|  |  | 8 | 21/05/2019 |  |  |  |  |  |  | 0,014 |  | 47 | 0,5 |  | C |  | 19 | B |  |  |  |  |  |  |
|  |  | 8 | 20/06/2019 |  |  |  |  |  |  | 0,014 | 38,6 | 45 | 0,5 | 0,8775 | C |  | 19 | B | 11 | 15.056 | 64.828 | 5 | 11 | 951 |
|  |  | 8 | 25/07/2019 |  |  |  |  |  |  | 0,014 |  | 67 | 0,5 |  | C |  | 16 | C |  |  |  |  |  |  |
|  |  | 8 | 20/08/2019 |  |  |  |  |  |  | 0,017 |  | 45 | 0,5 |  | C |  | 16 | B |  |  |  |  |  |  |
|  | 6 | 9 | 21/05/2018 | Main trafo | 3 | 1122170 | 2010 | 26.706 | Shandong | 0,014 |  | 58 | 0,5 |  | C |  | 11 | B |  |  |  |  |  |  |
|  |  | 9 | 28/06/2018 |  |  |  |  |  |  | 0,014 | 41,0 | 85 | 0,5 | 0,8805 | C |  | 8 | A | 18 | 11.431 | 48.283 | 13 | 700 | 1.512 |
|  |  | 9 | 24/07/2018 |  |  |  |  |  |  | 0,014 |  | 77 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 9 | 25/08/2018 |  |  |  |  |  |  | 0,017 |  | 82 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 9 | 25/09/2018 |  |  |  |  |  |  | 0,017 |  | 83 | 0,5 |  | C |  | 6 | A |  |  |  |  |  |  |
|  |  | 9 | 23/10/2018 |  |  |  |  |  |  | 0,017 |  | 78 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 9 | 22/11/2018 |  |  |  |  |  |  | 0,014 |  | 63 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 9 | 08/12/2018 |  |  |  |  |  |  | 0,014 |  | 83 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 23 | 21/05/2019 |  |  | 3011160192 | 2018 | 30.183 | PAUWES TRAFO | 0,011 |  | 93 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 23 | 20/06/2019 |  |  |  |  |  |  | 0,011 | 40,6 | 83 | 0,5 | 0,8786 | C |  | 8 | A | 3 | 9.903 | 31.346 | 6 | 156 | 369 |
|  |  | 23 | 25/07/2019 |  |  |  |  |  |  | 0,014 |  | 87 | 0,5 |  | C |  | 6 | A |  |  |  |  |  |  |
|  |  | 23 | 20/08/2019 |  |  |  |  |  |  | 0,011 |  | 78 | 0,5 |  | C |  | 6 | A |  |  |  |  |  |  |
|  | 7 | 10 | 21/05/2018 | Trafo UAT | 3 | 1035082 | 2010 | 4.749 | Shandong | 0,020 |  | 81 | 0,5 |  | C |  | 14 | B |  |  |  |  |  |  |
|  |  | 10 | 28/06/2018 |  |  |  |  |  |  | 0,022 | 37,5 | 79 | 0,5 | 0,8793 | C |  | 10 | A | 35 | 13.798 | 68.180 | 22 | 1.144 | 3.644 |
|  |  | 10 | 24/07/2018 |  |  |  |  |  |  | 0,020 |  | 76 | 0,5 |  | C |  | 11 | A |  |  |  |  |  |  |
|  |  | 10 | 25/08/2018 |  |  |  |  |  |  | 0,022 |  | 78 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 10 | 25/09/2018 |  |  |  |  |  |  | 0,020 |  | 75 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 10 | 23/10/2018 |  |  |  |  |  |  | 0,020 |  | 69 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 10 | 22/11/2018 |  |  |  |  |  |  | 0,022 |  | 80 | 0,5 |  | C |  | 11 | A |  |  |  |  |  |  |
|  |  | 10 | 08/12/2018 |  |  |  |  |  |  | 0,020 |  | 61 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |
|  |  | 22 | 21/05/2019 |  |  | PX18-0082 | 2018 | 12.000 | B & D | 0,014 |  | 85 | 0,5 |  | C |  | 5 | A |  |  |  |  |  |  |
|  |  | 22 | 20/06/2019 |  |  |  |  |  |  | 0,014 | 37,0 | 89 | 0,5 | 0,8798 | C |  | 5 | A | 4 | 10.251 | 34.223 | 16 | 39 | 232 |
|  |  | 22 | 25/07/2019 |  |  |  |  |  |  | 0,014 |  | 83 | 0,5 |  | C |  | 5 | A |  |  |  |  |  |  |
|  |  | 22 | 20/08/2019 |  |  |  |  |  |  | 0,014 |  | 78 | 0,5 |  | C |  | 4 | A |  |  |  |  |  |  |
|  | 8 | 11 | 21/05/2018 | Trafo 1 ESP | 3 | 007308428 | 2010 | 731 | Zhejian | 0,022 |  | 31 | 0,5 |  | C |  | 27 | D |  |  |  |  |  |  |
|  |  | 11 | 28/06/2018 |  |  |  |  |  |  | 0,022 | 35,0 | 60 | 0,5 | 0,8154 | C |  | 10 | B | 19 | 15.552 | 64.448 | 3 | 57 | 1.391 |
|  |  | 11 | 24/07/2018 |  |  |  |  |  |  | 0,020 |  | 53 | 0,5 |  | C |  | 9 | B |  |  |  |  |  |  |
|  |  | 11 | 25/08/2018 |  |  |  |  |  |  | 0,022 |  | 77 | 0,5 |  | C |  | 9 | B |  |  |  |  |  |  |
|  |  | 11 | 25/09/2018 |  |  |  |  |  |  | 0,020 |  | 64 | 0,5 |  | C |  | 10 | B |  |  |  |  |  |  |
|  |  | 11 | 23/10/2018 |  |  |  |  |  |  | 0,020 |  | 63 | 0,5 |  | C |  | 12 | B |  |  |  |  |  |  |
|  |  | 11 | 22/11/2018 |  |  |  |  |  |  | 0,020 |  | 53 | 0,5 |  | C |  | 9 | B |  |  |  |  |  |  |
|  |  | 11 | 08/12/2018 |  |  |  |  |  |  | 0,020 |  | 62 | 0,5 |  | C |  | 9 | B |  |  |  |  |  |  |
|  |  | 11 | 21/05/2019 |  |  |  |  |  |  | 0,022 |  | 85 | 0,5 |  | C |  | 9 | B |  |  |  |  |  |  |
|  |  | 11 | 20/06/2019 |  |  |  |  |  |  | 0,022 | 35,2 | 65 | 0,5 | 0,8212 | C |  | 9 | B | 11 | 19.448 | 64.974 | 6 | 15 | 1.064 |
|  |  | 11 | 25/07/2019 |  |  |  |  |  |  | 0,020 |  | 51 | 0,5 |  | C |  | 9 | B |  |  |  |  |  |  |
|  |  | 11 | 20/08/2019 |  |  |  |  |  |  | 0,020 |  | 69 | 0,5 |  | C |  | 8 | B |  |  |  |  |  |  |
|  | 9 | 12 | 21/05/2018 | Trafo 2 ESP | 3 | 007008428 | 2010 | 731 | Zhejian | 0,022 |  | 28 | 0,5 |  | C |  | 30 | E |  |  |  |  |  |  |
|  |  | 12 | 28/06/2018 |  |  |  |  |  |  | 0,025 | 30,2 | 34 | 0,5 | 0,8080 | C |  | 16 | C | 43 | 22.272 | 68.719 | 4 | 38 | 1.226 |
|  |  | 12 | 24/07/2018 |  |  |  |  |  |  | 0,022 |  | 30 | 0,5 |  | C |  | 25 | D |  |  |  |  |  |  |
|  |  | 12 | 25/08/2018 |  |  |  |  |  |  | 0,022 |  | 67 | 0,5 |  | C |  | 11 | C |  |  |  |  |  |  |
|  |  | 12 | 25/09/2018 |  |  |  |  |  |  | 0,022 |  | 31 | 0,5 |  | C |  | 32 | D |  |  |  |  |  |  |
|  |  | 12 | 23/10/2018 |  |  |  |  |  |  | 0,025 |  | 54 | 0,5 |  | C |  | 13 | B |  |  |  |  |  |  |
|  |  | 12 | 22/11/2018 |  |  |  |  |  |  | 0,025 |  | 33 | 0,5 |  | C |  | 38 | D |  |  |  |  |  |  |

|  | no | Test Cer. | Date Test | m cennix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MALAYSIAN LAB RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | nama unit |  |  |  |  |  | lpf (C) |  | dbpc | furan |  | metal in oil |  |  | corr. sul | keterangan |  |
|  |  |  |  |  |  | C2H6 | C2H4 | C2H2 | TOT | 25O | 100O |  |  | Al |  | Fe | Cu |  |  |  |
|  | Standa |  |  |  |  | r ethane | ethylene | acethylene |  | ASTM D924 |  | ASTM D2668 | ASTM D5837 |  | ASTM D3635 |  |  | ASTM D1275B |  |  |
|  |  |  |  |  |  | < 65 | <50 | < 2 | < 687 | < 0.1 | < 2.9 | > .2 | < 100 | 0,00 |  | 0,00 | 0,00 |  | Non corrosive |  |
|  |  | 8 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFIACTION |
|  |  | 8 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFIACTION |
|  |  | 8 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFIACTION |
|  |  | 8 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFIACTION |
|  |  | 8 | 20/06/2019 |  |  | 0 | 0 | 0 | 27 | 0,010 | 1,120 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 | 3A | Suspec Corrosive | Periodic condition monitoring |
|  |  | 8 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 8 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 6 | 9 | 21/05/2018 | Main trafo | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 9 | 28/06/2018 |  |  | 1 | 1 | 0 | 733 | 0,000 | 0,110 | 0,19 | 0 | 0,00 |  | 0,01 | 0,06 | 3 A | Suspec Corrosive | Add passivator |
|  |  | 9 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring Periodic condition monitoring Periodic condition monitoring |
|  |  | 9 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 9 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 9 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 9 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 9 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 23 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 23 | 20/06/2019 |  |  | 0 | 0 | 0 | 165 | 0,000 | 0,000 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 | 3A | Non corrosive | Periodic condition monitoring |
|  |  | 23 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 23 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 7 | 10 | 21/05/2018 | Trafo UAT | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 10 | 28/06/2018 |  |  | 5 | 7 | 1 | 1.214 | 0,000 | 0,140 | 0,21 | 0 | 0,00 |  | 0,01 | 0,11 | 3 A | Suspec Corrosive | Retest 6 months: DGA Add Passivator |
|  |  | 10 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 10 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring Periodic condition monitoring |
|  |  | 10 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 10 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 10 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 10 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 22 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 22 | 20/06/2019 |  |  | 26 | 2 | 0 | 87 | 0,000 | 0,120 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 |  |  | Periodic condition monitoring |
|  |  | 22 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 22 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 8 | 11 | 21/05/2018 | Trafo 1 ESP | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFICATION |
|  |  | 11 | 28/06/2018 |  |  | 0 | 0 | 0 | 79 | 0,000 | 0,050 | 0,16 | 0 | 0,00 |  | 0,00 | 0,02 | 1 B | Non corrosive | Retest 12 months: Specific Gravity Add Passivator |
|  |  | 11 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 11 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring (Purifying on end of July 2018) |
|  |  | 11 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 11 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 11 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 11 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 11 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 11 | 20/06/2019 |  |  | 0 | 0 | 0 | 32 | 0,000 | 0,060 | 0,16 | 0 | 0,00 |  | 0,00 | 0,02 | 2E | Non corrosive | Periodic condition monitoring |
|  |  | 11 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 11 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 9 | 12 | 21/05/2018 | Trafo 2 ESP | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFICATION |
|  |  | 12 | 28/06/2018 |  |  | 0 | 0 | 0 | 85 | 0,000 | 0,040 | 0,19 | 0 | 0,00 |  | 0,00 | 0,02 | 3 A | Suspec Corrosive | Retest 12 months: Specific Gravity Add Passivator |
|  |  | 12 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 12 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring (Purifying on end of July 2018) |
|  |  | 12 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 12 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 12 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform for Purification |

|  | no | Test Cer. | Date Test | nama unit |  | r | PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Standa |  |  |  |  |  |  |
|  |  |  |  |  |  |  | sekitar 70 |
|  |  | 8 | 23/10/2018 |  |  |  | GANTI MINYAK pada trafo ESP 3 Unit 1 dan ESP 2 Unit 2 For TEST 22 November 2018 Meskipun hampir semua trafo dalam keadaan prima, beberapa sudah mulai mengalami penurunan kondisi. PURIFIKASI Untuk ESP 1 dan 4 Unit 1, ESP 2 Unit 3 dan Ash Handling 1 ditemukan telah mengalami trend penuruan fungsi BDV dan Water Content. Purifikasi sebaiknya dilakukan dengan temperatur sekitar 700 agar mampu menghilangkan kandungan air dalam isolasi kertas. GANTI MINYAK Pada trafo ESP 3 Unit 1, ESP 2 dan 3 Unit 2 perlu dilakukan GANTI MINYAK, mengingat tingkat Acidity nya yang sudah tinggi. |
|  |  | 8 | 22/11/2018 |  |  |  |  |
|  |  | 8 | 08/12/2018 |  |  |  |  |
|  |  | 8 | 21/05/2019 |  |  |  |  |
|  |  | 8 | 20/06/2019 |  |  |  |  |
|  |  | 8 | 25/07/2019 |  |  |  |  |
|  |  | 8 | 20/08/2019 |  |  |  |  |
|  | 6 | 9 | 21/05/2018 | Main trafo | 3 |  |  |
|  |  | 9 | 28/06/2018 |  |  |  |  |
|  |  | 9 | 24/07/2018 |  |  |  |  |
|  |  | 9 | 25/08/2018 |  |  |  |  |
|  |  | 9 | 25/09/2018 |  |  |  |  |
|  |  | 9 | 23/10/2018 |  |  |  |  |
|  |  | 9 | 22/11/2018 |  |  |  |  |
|  |  | 9 | 08/12/2018 |  |  |  |  |
|  |  | 23 | 21/05/2019 |  |  |  |  |
|  |  | 23 | 20/06/2019 |  |  |  |  |
|  |  | 23 | 25/07/2019 |  |  |  |  |
|  |  | 23 | 20/08/2019 |  |  |  |  |
|  | 7 | 10 | 21/05/2018 | Trafo UAT | 3 |  |  |
|  |  | 10 | 28/06/2018 |  |  |  |  |
|  |  | 10 | 24/07/2018 |  |  |  |  |
|  |  | 10 | 25/08/2018 |  |  |  |  |
|  |  | 10 | 25/09/2018 |  |  |  |  |
|  |  | 10 | 23/10/2018 |  |  |  |  |
|  |  | 10 | 22/11/2018 |  |  |  |  |
|  |  | 10 | 08/12/2018 |  |  |  |  |
|  |  | 22 | 21/05/2019 |  |  |  |  |
|  |  | 22 | 20/06/2019 |  |  |  |  |
|  |  | 22 | 25/07/2019 |  |  |  |  |
|  |  | 22 | 20/08/2019 |  |  |  |  |
|  | 8 | 11 | 21/05/2018 | Trafo 1 ESP | 3 |  |  |
|  |  | 11 | 28/06/2018 |  |  |  |  |
|  |  | 11 | 24/07/2018 |  |  |  |  |
|  |  | 11 | 25/08/2018 |  |  |  |  |
|  |  | 11 | 25/09/2018 |  |  |  |  |
|  |  | 11 | 23/10/2018 |  |  |  |  |
|  |  | 11 | 22/11/2018 |  |  |  |  |
|  |  | 11 | 08/12/2018 |  |  |  |  |
|  |  | 11 | 21/05/2019 |  |  |  |  |
|  |  | 11 | 20/06/2019 |  |  |  |  |
|  |  | 11 | 25/07/2019 |  |  |  |  |
|  |  | 11 | 20/08/2019 |  |  |  |  |
|  | 9 | 12 | 21/05/2018 | Trafo 2 ESP | 3 |  |  |
|  |  | 12 | 28/06/2018 |  |  |  |  |
|  |  | 12 | 24/07/2018 |  |  |  |  |
|  |  | 12 | 25/08/2018 |  |  |  |  |
|  |  | 12 | 25/09/2018 |  |  |  |  |
|  |  | 12 | 23/10/2018 |  |  |  |  |
|  |  | 12 | 22/11/2018 |  |  |  |  |

|  | no | Test Cer. | Date Test | m cennix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MALAYSIAN LAB RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | nama unit |  |  |  |  |  | lpf (C) |  | dbpc | furan |  | metal in oil |  |  | corr. sul | keterangan |  |
|  |  |  |  |  |  | C2H6 | C2H4 | C2H2 | TOT | 25O | 100O |  |  | Al |  | Fe | Cu |  |  |  |
|  | Standa |  |  |  |  | r ethane | ethylene | acethylene |  | ASTM D924 |  | ASTM D2668 | ASTM D5837 |  | ASTM D3635 |  |  | ASTM D1275B |  |  |
|  |  |  |  |  |  | < 65 | <50 | < 2 | < 687 | < 0.1 | < 2.9 | > .2 | < 100 | 0,00 |  | 0,00 | 0,00 |  | Non corrosive |  |
|  |  | 12 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform for Purification |
|  |  | 12 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 12 | 20/06/2019 |  |  | 0 | 0 | 0 | 68 | 0,000 | 0,010 | 0,19 | 180 | 0,00 |  | 0,00 | 0,02 | 3A | Non corrosive | Periodic condition monitoring |
|  |  | 12 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Preparing for Purification |
|  |  | 12 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Preparing for Purification |
|  | 10 | 13 | 21/05/2018 | Trafo 3 ESP | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFICATION |
|  |  | 13 | 28/06/2018 |  |  | 0 | 0 | 0 | 99 | 0,000 | 0,010 | 0,20 | 4 | 0,00 |  | 0,00 | 0,02 | 2 E | Non corrosive | Retest 12 months: Specific Gravity Retest 6 months: Dielectric and Water Content Add Passivator |
|  |  | 13 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFICATION |
|  |  | 13 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring (Purifying on end of July 2018) |
|  |  | 13 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFICATION |
|  |  | 13 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 13 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 13 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 13 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ReTest in 6 months : Water Content and BDV - Prepare for PURIFICATION |
|  |  | 13 | 20/06/2019 |  |  | 0 | 0 | 0 | 106 | 0,000 | 0,070 | 0,19 | 0 | 0,00 |  | 0,00 | 0,02 | 2E | Non corrosive | ReTest in 6 months : Water Content and BDV - Prepare for PURIFICATION |
|  |  | 13 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Preparing for Purification |
|  |  | 13 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 11 | 14 | 21/05/2018 | Trafo 4 ESP | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Retest 6 months: Dielectric and Water Content |
|  |  | 14 | 28/06/2018 |  |  | 0 | 0 | 0 | 44 | 0,000 | 0,550 | 0,00 | 0 | 0,00 |  | 0,03 | 0,02 | 1 B | Non corrosive | Add inhibitor 2,6-DBPC and PASSIVATOR |
|  |  | 14 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 14 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring (Purifying on end of July 2018) |
|  |  | 14 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 14 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 14 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 14 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 14 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 14 | 20/06/2019 |  |  | 0 | 0 | 0 | 60 | 0,000 | 0,490 | 0,00 | 0 | 0,00 |  | 0,03 | 0,01 | 1B | Non corrosive | Periodic condition monitoring |
|  |  | 14 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 14 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 12 | 15 | 21/05/2018 | Ash Handling |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 15 | 28/06/2018 |  |  | 9 | 8 | 0 | 647 | 0,000 | 0,460 | 0,22 | 0 | 0,00 |  | 0,01 | 0,04 | 1 B | Non corrosive | Add passivator |
|  |  | 15 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring Periodic condition monitoring Periodic condition monitoring |
|  |  | 15 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 15 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 15 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 15 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Monitoring : Water Content and BDV - Prepare for PURIFICATION |
|  |  | 15 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Retest in 6 months : Water Content and BDV - Prepare for PURIFICATION |
|  |  | 15 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform for PURIFICATION |
|  |  | 15 | 20/06/2019 |  |  | 0 | 11 | 0 | 564 | 0,000 | 0,360 | 0,21 | 0 | 0,00 |  | 0,00 | 0,02 | 2e | Non corrosive | Perform for PURIFICATION |
|  |  | 15 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 15 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 13 | 16 | 21/05/2018 | Ash Handling |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFICATION |
|  |  | 16 | 28/06/2018 |  |  | 0 | 5 | 0 | 290 | 0,000 | 0,490 | 0,20 | 0 | 0,00 |  | 0,00 | 0,02 | 3 A | Suspec Corrosive | Retest 6 months: DGA Add Passivator |
|  |  | 16 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL PURIFICATION |
|  |  | 16 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring (Purifying on end of July 2018) |
|  |  | 16 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 16 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |

|  | no | Test Cer. | Date Test | nama unit |  | r | PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Standa |  |  |  |  |  |  |
|  |  | 12 | 08/12/2018 |  |  |  |  |
|  |  | 12 | 21/05/2019 |  |  |  |  |
|  |  | 12 | 20/06/2019 |  |  |  |  |
|  |  | 12 | 25/07/2019 |  |  |  |  |
|  |  | 12 | 20/08/2019 |  |  |  |  |
|  | 10 | 13 | 21/05/2018 | Trafo 3 ESP | 3 |  |  |
|  |  | 13 | 28/06/2018 |  |  |  |  |
|  |  | 13 | 24/07/2018 |  |  |  |  |
|  |  | 13 | 25/08/2018 |  |  |  |  |
|  |  | 13 | 25/09/2018 |  |  |  |  |
|  |  | 13 | 23/10/2018 |  |  |  |  |
|  |  | 13 | 22/11/2018 |  |  |  |  |
|  |  | 13 | 08/12/2018 |  |  |  |  |
|  |  | 13 | 21/05/2019 |  |  |  |  |
|  |  | 13 | 20/06/2019 |  |  |  |  |
|  |  | 13 | 25/07/2019 |  |  |  |  |
|  |  | 13 | 20/08/2019 |  |  |  |  |
|  | 11 | 14 | 21/05/2018 | Trafo 4 ESP | 3 |  |  |
|  |  | 14 | 28/06/2018 |  |  |  |  |
|  |  | 14 | 24/07/2018 |  |  |  |  |
|  |  | 14 | 25/08/2018 |  |  |  |  |
|  |  | 14 | 25/09/2018 |  |  |  |  |
|  |  | 14 | 23/10/2018 |  |  |  |  |
|  |  | 14 | 22/11/2018 |  |  |  |  |
|  |  | 14 | 08/12/2018 |  |  |  |  |
|  |  | 14 | 21/05/2019 |  |  |  |  |
|  |  | 14 | 20/06/2019 |  |  |  |  |
|  |  | 14 | 25/07/2019 |  |  |  |  |
|  |  | 14 | 20/08/2019 |  |  |  |  |
|  | 12 | 15 | 21/05/2018 | Ash Handling |  |  |  |
|  |  | 15 | 28/06/2018 |  |  |  |  |
|  |  | 15 | 24/07/2018 |  |  |  |  |
|  |  | 15 | 25/08/2018 |  |  |  |  |
|  |  | 15 | 25/09/2018 |  |  |  |  |
|  |  | 15 | 23/10/2018 |  |  |  |  |
|  |  | 15 | 22/11/2018 |  |  |  |  |
|  |  | 15 | 08/12/2018 |  |  |  |  |
|  |  | 15 | 21/05/2019 |  |  |  |  |
|  |  | 15 | 20/06/2019 |  |  |  |  |
|  |  | 15 | 25/07/2019 |  |  |  |  |
|  |  | 15 | 20/08/2019 |  |  |  |  |
|  | 13 | 16 | 21/05/2018 | Ash Handling |  |  |  |
|  |  | 16 | 28/06/2018 |  |  |  |  |
|  |  | 16 | 24/07/2018 |  |  |  |  |
|  |  | 16 | 25/08/2018 |  |  |  |  |
|  |  | 16 | 25/09/2018 |  |  |  |  |
|  |  | 16 | 23/10/2018 |  |  |  |  |

|  | no | Test Cer. | Date Test | m cennix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MALAYSIAN LAB RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | nama unit |  |  |  |  |  | lpf (C) |  | dbpc | furan |  | metal in oil |  |  | corr. sul | keterangan |  |
|  |  |  |  |  |  | C2H6 | C2H4 | C2H2 | TOT | 25O | 100O |  |  | Al |  | Fe | Cu |  |  |  |
|  | Standa |  |  |  |  | r ethane | ethylene | acethylene |  | ASTM D924 |  | ASTM D2668 | ASTM D5837 |  | ASTM D3635 |  |  | ASTM D1275B |  |  |
|  |  |  |  |  |  | < 65 | <50 | < 2 | < 687 | < 0.1 | < 2.9 | > .2 | < 100 | 0,00 |  | 0,00 | 0,00 |  | Non corrosive |  |
|  |  | 16 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 16 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 16 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 16 | 20/06/2019 |  |  | 11 | 9 | 0 | 519 | 0,000 | 0,680 | 0,20 | 0 | 0,01 |  | 0,00 | 0,02 | 3A | Non corrosive | Periodic condition monitoring |
|  |  | 16 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 16 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 14 | 17 17 17 17 17 17 17 17 17 17 17 | 21/05/2018 | Trafo 1 ESP | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | OIL PURIFICATION |
|  |  |  | 28/06/2018 |  |  | 0 | 2 | 0 | 157 | 0,030 | 3,420 | 0,00 | 0 | 0,00 |  | 0,06 | 0,03 | 2 C | Non corrosive | Add inhibitor 2,6-DBPC and PASSIVATOR |
|  |  |  | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  |  | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  |  | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  |  | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  |  | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  |  | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  |  | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  |  | 20/06/2019 |  |  | 0 | 0 | 0 | 117 | 0,000 | 0,720 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 | 3A | Non corrosive | Monitoring : Acidity, IFT and LPF |
|  |  |  | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 17 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 15 | 18 | 21/05/2018 | Trafo 2 ESP | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Retest 6 months: Acidity and IFT |
|  |  | 18 | 28/06/2018 |  |  | 0 | 0 | 0 | 80 | 0,000 | 0,680 | 0,00 | 42 | 0,00 |  | 0,00 | 0,02 | 3 A | Suspec Corrosive | Add inhibitor 2,6-DBPC and PASSIVATOR |
|  |  | 18 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 18 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 18 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 18 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 18 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 18 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 18 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 18 | 20/06/2019 |  |  | 0 | 0 | 0 | 35 | 0,000 | 0,450 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 | 3A | Non corrosive | Perform OIL REGENERATION |
|  |  | 18 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 18 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  | 16 | 19 | 21/05/2018 | Trafo 3 ESP | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Retest 6 months: Acidity and IFT |
|  |  | 19 | 28/06/2018 |  |  | 0 | 0 | 0 | 65 | 0,000 | 0,570 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 | 3 A | Suspec Corrosive | Perform OIL REGENERATION |
|  |  | 19 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 19 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 19 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 19 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 19 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 19 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 19 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 19 | 20/06/2019 |  |  | 0 | 0 | 0 | 79 | 0,010 | 0,790 | 0,00 | 0 | 0,00 |  | 0,00 | 0,02 | 3A | Non corrosive | Perform OIL REGENERATION |
|  |  | 19 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  |  | 19 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Perform OIL REGENERATION |
|  | 17 | 20 | 21/05/2018 | Trafo 4 ESP | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 20 | 28/06/2018 |  |  | 0 | 0 | 0 | 112 | 0,000 | 1,620 | 0,01 | 0 | 0,00 |  | 0,00 | 0,03 | 2 C | Non corrosive | Add inhibitor 2,6-DBPC and PASSIVATOR |
|  |  | 20 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 20 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 20 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 20 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 20 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 20 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 20 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 20 | 20/06/2019 |  |  | 0 | 0 | 0 | 72 | 0,020 | 1,150 | 0,01 | 7 | 0,00 |  | 0,00 | 0,02 | 2C | Non corrosive | Monitoring : Acidity, IFT and LPF |
|  |  | 20 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |

|  | no | Test Cer. | Date Test | nama unit |  | r | PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Standa |  |  |  |  |  |  |
|  |  | 16 | 22/11/2018 |  |  |  |  |
|  |  | 16 | 08/12/2018 |  |  |  |  |
|  |  | 16 | 21/05/2019 |  |  |  |  |
|  |  | 16 | 20/06/2019 |  |  |  |  |
|  |  | 16 | 25/07/2019 |  |  |  |  |
|  |  | 16 | 20/08/2019 |  |  |  |  |
|  | 14 | 17 17 17 17 17 17 17 17 17 17 17 | 21/05/2018 | Trafo 1 ESP | 2 |  |  |
|  |  |  | 28/06/2018 |  |  |  |  |
|  |  |  | 24/07/2018 |  |  |  |  |
|  |  |  | 25/08/2018 |  |  |  |  |
|  |  |  | 25/09/2018 |  |  |  |  |
|  |  |  | 23/10/2018 |  |  |  |  |
|  |  |  | 22/11/2018 |  |  |  |  |
|  |  |  | 08/12/2018 |  |  |  |  |
|  |  |  | 21/05/2019 |  |  |  |  |
|  |  |  | 20/06/2019 |  |  |  |  |
|  |  |  | 25/07/2019 |  |  |  |  |
|  |  | 17 | 20/08/2019 |  |  |  |  |
|  | 15 | 18 | 21/05/2018 | Trafo 2 ESP | 2 |  |  |
|  |  | 18 | 28/06/2018 |  |  |  |  |
|  |  | 18 | 24/07/2018 |  |  |  |  |
|  |  | 18 | 25/08/2018 |  |  |  |  |
|  |  | 18 | 25/09/2018 |  |  |  |  |
|  |  | 18 | 23/10/2018 |  |  |  |  |
|  |  | 18 | 22/11/2018 |  |  |  |  |
|  |  | 18 | 08/12/2018 |  |  |  |  |
|  |  | 18 | 21/05/2019 |  |  |  |  |
|  |  | 18 | 20/06/2019 |  |  |  |  |
|  |  | 18 | 25/07/2019 |  |  |  |  |
|  |  | 18 | 20/08/2019 |  |  |  |  |
|  | 16 | 19 | 21/05/2018 | Trafo 3 ESP | 2 |  |  |
|  |  | 19 | 28/06/2018 |  |  |  |  |
|  |  | 19 | 24/07/2018 |  |  |  |  |
|  |  | 19 | 25/08/2018 |  |  |  |  |
|  |  | 19 | 25/09/2018 |  |  |  |  |
|  |  | 19 | 23/10/2018 |  |  |  |  |
|  |  | 19 | 22/11/2018 |  |  |  |  |
|  |  | 19 | 08/12/2018 |  |  |  |  |
|  |  | 19 | 21/05/2019 |  |  |  |  |
|  |  | 19 | 20/06/2019 |  |  |  |  |
|  |  | 19 | 25/07/2019 |  |  |  |  |
|  |  | 19 | 20/08/2019 |  |  |  |  |
|  | 17 | 20 | 21/05/2018 | Trafo 4 ESP | 2 |  |  |
|  |  | 20 | 28/06/2018 |  |  |  |  |
|  |  | 20 | 24/07/2018 |  |  |  |  |
|  |  | 20 | 25/08/2018 |  |  |  |  |
|  |  | 20 | 25/09/2018 |  |  |  |  |
|  |  | 20 | 23/10/2018 |  |  |  |  |
|  |  | 20 | 22/11/2018 |  |  |  |  |
|  |  | 20 | 08/12/2018 |  |  |  |  |
|  |  | 20 | 21/05/2019 |  |  |  |  |
|  |  | 20 | 20/06/2019 |  |  |  |  |
|  |  | 20 | 25/07/2019 |  |  |  |  |

|  | no | Test Cer. | Date Test | nama unit |  | Serial number | thn opr | Jumlah minyak, liter | Buatan |  |  |  |  |  |  |  |  |  |  |  |  |  | hasil test laboratorium |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  | acid | ift | diel. | color | spec. Graf. | visual | sedi. | moisture |  |  |  |  |  | dga ASTM D3612 |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ppm | grade | H2 | O2 | N2 | CH4 | CO | CO2 |
|  |  |  | Standard yang dipakai |  |  |  |  |  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | ASTM D1533 |  | hydrogen | oksigen | nitrogen | methane | carbon monoksida | carbon dioksida |
|  |  |  |  |  |  |  |  | BATASAN OPERASI |  | < 0,06 | > 32 | > 30 | < 3,5 | > 0,84 | C |  | < 20 |  | < 100 |  |  | < 120 | < 350 | < 2.500 |
|  |  | 20 | 20/08/2019 |  |  |  |  |  |  | 0,036 |  | 45 | 1,5 |  | C |  | 12 | B |  |  |  |  |  |  |
|  | 18 | 21 | 21/05/2018 | Main Trafo | 2 | 1006902 | 2011 | 11.160 | Wolong | 0,011 |  | 46 | 0,5 |  | C |  | 14 | B |  |  |  |  |  |  |
|  |  | 21 | 28/06/2018 |  |  |  |  |  |  | 0,008 | 42,1 | 75 | 0,5 | 0,8663 | C |  | 10 | B | 19 | 12.733 | 53.386 | 10 | 193 | 2.448 |
|  |  | 21 | 24/07/2018 |  |  |  |  |  |  | 0,011 |  | 79 | 0,5 |  | C |  | 11 | B |  |  |  |  |  |  |
|  |  | 21 | 25/08/2018 |  |  |  |  |  |  | 0,011 |  | 83 | 0,5 |  | C |  | 9 | A |  |  |  |  |  |  |
|  |  | 21 | 25/09/2018 |  |  |  |  |  |  | 0,011 |  | 90 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 21 | 23/10/2018 |  |  |  |  |  |  | 0,011 |  | 64 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 21 | 22/11/2018 |  |  |  |  |  |  | 0,011 |  | 61 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 21 | 08/12/2018 |  |  |  |  |  |  | 0,011 |  | 57 | 0,5 |  | C |  | 6 | A |  |  |  |  |  |  |
|  |  | 21 | 21/05/2019 |  |  |  |  |  |  | 0,011 |  | 63 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 21 | 20/06/2019 |  |  |  |  |  |  | 0,011 | 39,3 | 58 | 0,5 | 0,8745 | C |  | 11 | A | 10 | 17.382 | 50.681 | 8 | 107 | 712 |
|  |  | 21 | 25/07/2019 |  |  |  |  |  |  | 0,011 |  | 49 | 0,5 |  | C |  | 7 | A |  |  |  |  |  |  |
|  |  | 21 | 20/08/2019 |  |  |  |  |  |  | 0,014 |  | 36 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |  |

|  | no | Test Cer. | Date Test | m cennix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MALAYSIAN LAB RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | nama unit |  |  |  |  |  | lpf (C) |  | dbpc | furan |  | metal in oil |  |  | corr. sul | keterangan |  |
|  |  |  |  |  |  | C2H6 | C2H4 | C2H2 | TOT | 25O | 100O |  |  | Al |  | Fe | Cu |  |  |  |
|  |  |  | Standa |  |  | r ethane | ethylene | acethylene |  | ASTM D924 |  | ASTM D2668 | ASTM D5837 |  | ASTM D3635 |  |  | ASTM D1275B |  |  |
|  |  |  |  |  |  | < 65 | <50 | < 2 | < 687 | < 0.1 | < 2.9 | > .2 | < 100 | 0,00 |  | 0,00 | 0,00 |  | Non corrosive |  |
|  |  | 20 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  | 18 | 21 | 21/05/2018 | Main Trafo | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 21 | 28/06/2018 |  |  | 0 | 2 | 0 | 224 | 0,000 | 0,410 | 0,22 | 113 | 0,00 |  | 0,00 | 0,03 | 1 B | Non corrosive | Retest 6 months: Furan and DGA Add Passivator |
|  |  | 21 | 24/07/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic Condition monitoring |
|  |  | 21 | 25/08/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 21 | 25/09/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 21 | 23/10/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 21 | 22/11/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 21 | 08/12/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 21 | 21/05/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 21 | 20/06/2019 |  |  | 0 | 2 | 0 | 127 | 0,010 | 0,730 | 0,22 | 0 | 0,00 |  | 0,00 | 0,02 | 2E | Non corrosive | Periodic condition monitoring |
|  |  | 21 | 25/07/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |
|  |  | 21 | 20/08/2019 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Periodic condition monitoring |

Summary by Soetjahjono

TxM Indonesia

|  | no | Test Cer. | Date Test | nama unit |  | r | PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Standa |  |  |  |  |
|  |  | 20 | 20/08/2019 |  |  |  |  |
|  | 18 | 21 | 21/05/2018 | Main Trafo | 2 |  |  |
|  |  | 21 | 28/06/2018 |  |  |  |  |
|  |  | 21 | 24/07/2018 |  |  |  |  |
|  |  | 21 | 25/08/2018 |  |  |  |  |
|  |  | 21 | 25/09/2018 |  |  |  |  |
|  |  | 21 | 23/10/2018 |  |  |  |  |
|  |  | 21 | 22/11/2018 |  |  |  |  |
|  |  | 21 | 08/12/2018 |  |  |  |  |
|  |  | 21 | 21/05/2019 |  |  |  |  |
|  |  | 21 | 20/06/2019 |  |  |  |  |
|  |  | 21 | 25/07/2019 |  |  |  |  |
|  |  | 21 | 20/08/2019 |  |  |  |  |