LAPORAN UJI MINYAK TRAFO

di

UNIT JASA PEMBANGKIT

JERANJANG

Yang dilakukan pada tanggal 07 Desember 2017

Untuk keadaan trafo bulan DESEMBER 2017

1.0 Table of Contents 	Page

1.0 	Specific Information 	2

2.0 	Our Comments and Recommendations of the Test Results  Analysis

- Transformer Unit MAIN TRAFO UNIT 1 (S/N: 1006901) 	3

Test Certificate 4

- Transformer Unit TRAFO 1 ESP UNIT 1 (S/N: 10937) 	5

Test Certificate 5

- Transformer Unit TRAFO 2 ESP UNIT 1 (S/N: 10035) 	7

Test Certificate 6

- Transformer Unit TRAFO 3 ESP UNIT 1 (S/N: 10031) 	9

Test Certificate 7

- Transformer Unit TRAFO 4 ESP UNIT 1 (S/N: 10034) 	11

Test Certificate 8

- Transformer Unit MAIN TRAFO UNIT 3 (S/N: 1122170) 	13

Test Certificate 9

- Transformer Unit UAT 3 (S/N: 1035082) 	14

Test Certificate 10

- Transformer Unit TRAFO 1 ESP UNIT 3 (S/N: 007308428) 	15

Test Certificate 11

- Transformer Unit TRAFO 2 ESP UNIT 3 (S/N: 0070084208) 	17

Test Certificate 12

- Transformer Unit TRAFO 3 ESP UNIT 3 (S/N: 0072084208) 	19

Test Certificate 13

- Transformer Unit TRAFO 4 UNIT 3 (S/N: 0071084208) 	21

Test Certificate 14

- Transformer Unit ASH HANDLING (S/N: 10820108) 	23

Test Certificate 15

- Transformer Unit ASH HANDLING (S/N: 10820107) 	24

Test Certificate 16

3.0 	Summary of Recommendation 	25

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the

Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information herein

Page 1 of 25

1.0 	Specific Information:

| No. | Unit No. | Serial Number | TC | Test Requested |
| --- | --- | --- | --- | --- |
| 1. | MAIN TRAFO UNIT 1 | 1006901 | 4 | OLTT+ and Corrosive Sulfur |
| 2. | TRAFO 1 ESP UNIT 1 | 10937 | 5 | OLTT+ and Corrosive Sulfur |
| 3. | TRAFO 2 ESP UNIT 1 | 10035 | 6 | OLTT+ and Corrosive Sulfur |
| 4. | TRAFO 3 ESP UNIT 1 | 10031 | 7 | OLTT+ and Corrosive Sulfur |
| 5. | TRAFO 4 ESP UNIT 1 | 10034 | 8 | OLTT+ and Corrosive Sulfur |
| 6. | MAIN TRAFO UNIT 3 | 1122170 | 9 | OLTT+ and Corrosive Sulfur |
| 7. | UAT 3 | 1035082 | 10 | OLTT+ and Corrosive Sulfur |
| 8. | TRAFO 1 ESP UNIT 3 | 007308428 | 11 | OLTT+ and Corrosive Sulfur |
| 9. | TRAFO 2 ESP UNIT 3 | 0070084208 | 12 | OLTT+ and Corrosive Sulfur |
| 10. | TRAFO 3 ESP UNIT 3 | 0072084208 | 13 | OLTT+ and Corrosive Sulfur |
| 11. | TRAFO 4 UNIT 3 | 0071084208 | 14 | OLTT+ and Corrosive Sulfur |
| 12. | ASH HANDLING | 10820108 | 15 | OLTT+ and Corrosive Sulfur |
| 13. | ASH HANDLING | 10820107 | 16 | OLTT+ and Corrosive Sulfur |

Note:

* OLTT+ consists of Liquid Screen Tests, Dissolved Gas Analysis (DGA), Water     Content, Furan Analysis, Metals-in-Oil Analysis, Liquid Power Factors, and Inhibitor       Content (DBPC).

** Liquid Screen Test consists of Acidity, Interfacial Tension (IFT), Dielectric, Colour,          Specific Gravity, Visualization, and Sediment.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the

Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information herein

Page 2 of 25

2.0 Our Comments and Recommendations of The Test Results Analysis:  We had reviewed each laboratory test result against respective benchmark parameter and following are our comments and recommendations.

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 1. | MAIN TRAFO UNIT 1 | 1006901 | 4 |

A) Analysis

- Acidity of 0.011mgKOH/g and IFT of 40.2mN/m are ACCEPTABLE.

- Dielectric of 87kV is ACCEPTABLE.

- Specific gravity, Colour, and Visualization of oil is in the ACCEPTABLE range.

- DGA shows increasing in volume for Hydrogen, Carbon Monoxide and

Carbon Dioxide. High Hydrogen and Carbon Oxides in a transformer’s oil is an indication that the transformer is afflicted with a partial discharge condition. It is advisable to consult transformer manufacturer to ascertain the cause of fault gases buildup in the transformer.

- Water Content in oil of 7ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 0.46% M/dw is graded as A. For this transformer, it is recommended to maintain water content in oil at less than 20ppm.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.27% by weight is detected, thus ACCEPTABLE.

- Tested on copper strip resultant in multicolored with lavender blue and/or silver overlaid on claret red, thus Non-corrosive of 2C.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 3 of 25

B) Recommendation

- Retest for DGA in 6 months to diagnose any possible fault and establish trend of the gases.

- Add passivator before the sulfur convert to be corrosive enough to attack copper. Passivator would coat the copper surface to retard or delay attack by corrosive sulfur.

- Other parameters: Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-In-Oil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 4 of 25

### CENNIX LABORATORY (M) SDN BHD	     4

#### (Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE	STATUS	OIL TEMP °C	W. TEMP °C	OIL LEVEL	PAINT	S. GEL	LEAKS

04/07/2017	ONLINE	45	NORMAL	GOOD

31/07/2017	ONLINE	28	28

30/08/2017	OFFLINE	49	49	NORMAL	FAIR	GOOD	NONE

29/09/2017	OFFLINE	48	NORMAL	FAIR	GOOD	NONE

30/10/2017	ONLINE	60	64	NORMAL	FAIR	GOOD	NONE

27/11/2017	ONLINE	51

06/12/2017	OFFLINE	50	48

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

04/07/2017	ROUTINE	    0.017 AC	41.5 AC	58 AC	   0.5 AC	     	0.8691 AC	CLEAR AC

31/07/2017	ROUTINE	    0.017 AC	 	70 AC	   0.5 AC	     	 	CLEAR AC

30/08/2017	ROUTINE	    0.017 AC	 	92 AC	   0.5 AC	     	 	CLEAR AC

29/09/2017	ROUTINE	    0.014 AC	 	82 AC	   0.5 AC	     	 	CLEAR AC

30/10/2017	ROUTINE	    0.014 AC	 	79 AC	   0.5 AC	     	 	CLEAR AC

27/11/2017	ROUTINE	    0.014 AC	 	53 AC	   0.5 AC	     	 	CLEAR AC

06/12/2017	ROUTINE	    0.011 AC	40.2 AC	87 AC	   0.5 AC	     	0.8745 AC	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

| 04/07/2017 | 147 | 9471 | 43278 | 32 | 655 | 2728 | 4 | 5 | ND | 843 | 56320 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 06/12/2017 | 183 | 12895 | 43794 | 39 | 715 | 3166 | 5 | 5 | ND | 947 | 60802 |

RECOMMENDATION:

RETEST 6 MONTHS:

THE DETECTION OF HYDROGEN IN CONJUNCTION WITH CARBON OXIDES MIGHT BE AN INDICATIVE OF LOW ENERGY DISCHARGE-CORONA INVOLVING SOLID INSULATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	33	10	0.82	A

31/07/2017	26	8	1.04	B

30/08/2017	34	6	0.49	A

29/09/2017	36	8	0.57	A

30/10/2017	44	10	0.45	A

27/11/2017	42	8	0.40	A

06/12/2017	38	7	0.46	A

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - MAIN TRAFO UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

| MFG | - WOLONG |
| --- | --- |
| DATE MFG | - 2011 |
| MAIN TANK S/N | - 100691 |
| KVA | - 40000 |
| PRI | - 165000 V |
| SEC | - 6300 V |
| KILOGRAMS | - 81000 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - OFAF |
| IMPEDENCE | - 13.1% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 30857 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - YES H2O COOLED	 - NO OIL PUMPS	 - YES TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - YES BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

###### DATE	SERVICE

CENNIX LABORATORY SDN BHD 4 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | ND | ND | ND | ND |
| 06/12/2017 | ND | ND | ND | ND | ND | ND |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  0.02	  0.01	  0.01

06/12/2017	  ND	  0.01	  0.04

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	0.140 AC	04/07/2017	0.24 AC

06/12/2017	0.000 AC	 	0.040 AC	06/12/2017	0.27 AC

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	3A	MAGENTA

06/12/2017	NON-COR	2C	LAVENDER BLUE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - MAIN TRAFO UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - WOLONG

DATE MFG	 - 2011

MAIN TANK S/N	 - 100691

KVA	 - 40000

PRI	 - 165000 V

SEC	 - 6300 V

KILOGRAMS	 - 81000

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - OFAF

IMPEDENCE	 - 13.1%

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 30857

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - YES H2O COOLED	 - NO OIL PUMPS	 - YES TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - YES BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 2. | TRAFO 1 ESP UNIT 1 | 10937 | 5 |

A) Analysis

- Acidity of 0.062mgKOH/g is QUESTIONABLE whereas IFT of 25.0mN/m is UNACCEPTABLE. These two parameters indicate the oil is deteriorated. Remove the unwanted acids which actively promote more acid and oxidation by-product, to avoid more accumulation of contaminants in the oil that will weaken the oil interfacial tension.

- Dielectric of 48kV is ACCEPTABLE.

- Colour, Specific Gravity, and Visualization for the oil are within the ACCEPTABLE range.

- DGA indicates the transformer is operating satisfactorily, without significant amount of combustible gases being generated.

- Water content in oil of 18ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.89% M/dw is graded as D. For this transformer, it is advisable to maintain the water content level below 20ppm.

- Furanic compound 2FOL of 75ppb was detected which indicates the solid insulation is wet. It is important to maintain the oil in a good condition so as not to further deteriorate the paper insulation.

- Metals-In-Oil were not detected, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- No inhibitor content is detectable, thus UNACCEPTABLE. Lack of inhibitor content will accelerate the oxidation process which produces acid and sludge. These oxidation by-products are depositing and degrading the oil as well as the paper insulation.

- Corrosive sulfur test on copper strip resultant in light orange, thus Noncorrosive of 1A.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 5 of 25

#### Ref No : TXM/MKT-1200/SA/CI17049

B) Recommendation

- It is recommended to perform Transformer Oil Regeneration on this unit. Transformer oil regeneration at this stage of contamination will effectively remove unwanted oxidation byproducts as well as moisture from the insulating oil. This process will restore the oil back to its original quality, thus protecting the paper insulation and extending the transformer serviceable lifespan. Furthermore, oil inhibitor 2,6-DBPC and passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 6 of 25

## CENNIX LABORATORY (M) SDN BHD	     5

#### (Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE	STATUS	OIL TEMP °C	W. TEMP °C	OIL LEVEL	PAINT	S. GEL	LEAKS

04/07/2017	36	NORMAL	GOOD

31/07/2017	OFFLINE	28

30/08/2017	OFFLINE	30	GOOD	NONE

29/09/2017	OFFLINE	35	NORMAL	GOOD	NONE

30/10/2017	OFFLINE	50	NORMAL	GOOD	NONE

27/11/2017	ONLINE

06/12/2017	OFFLINE

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

04/07/2017	ROUTINE	    0.056 QU	25.3 UN	50 AC	   1.5 AC	     	0.8529 AC	CLEAR AC

31/07/2017	ROUTINE	    0.059 QU	 	57 AC	   1.5 AC	     	 	CLEAR AC

30/08/2017	ROUTINE	    0.056 QU	 	65 AC	   1.5 AC	     	 	CLEAR AC

29/09/2017	ROUTINE	    0.059 QU	 	58 AC	   1.5 AC	     	 	CLEAR AC

30/10/2017	ROUTINE	    0.059 QU	 	23 UN	   1.5 AC	     	 	CLEAR AC

27/11/2017	ROUTINE	    0.062 QU	 	25 QU	   1.5 AC	     	 	CLEAR AC

06/12/2017	ROUTINE	    0.062 QU	25.0 UN	48 AC	   1.5 AC	     	0.8583 AC	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	35	20494	67487	4	69	1143	ND	1	ND	109	89233

06/12/2017	39	19933	67198	4	83	1261	ND	1	ND	127	88519

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	26	18	2.34	D

31/07/2017	25	20	2.60	D

30/08/2017	29	18	1.89	D

29/09/2017	32	19	1.80	D

30/10/2017	42	32	1.60	C

27/11/2017	41	33	1.65	C

06/12/2017	30	18	1.89	D

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 1 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - FUJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 10937

KVA	 -

PRI	 - 72000 V

SEC	 - 380 V

KILOGRAMS	 - 1000

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 630

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 3. | TRAFO 2 ESP UNIT 1 | 10035 | 6 |

A) Analysis

- Acidity of 0.053mgKOH/g is QUESTIONABLE while IFT of 27.3mN/m is UNACCEPTABLE. These two parameters indicate there are further accumulation of oxidation byproducts in the oil.  Oil oxidation byproducts promotes more acids to be produced by the present acids. Therefore, removal of these contaminations is highly recommended.

- Dielectric of 51kV is ACCEPTABLE.

- Colour, Specific Gravity, and Visualization for the oil are within the ACCEPTABLE range.

- DGA indicates the transformer is operating satisfactorily, without significant amount of combustible gases being generated.

- Water content in oil of 17ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.78% M/dw is graded as D. For this transformer, it is advisable to maintain the water content level below 20ppm.

- Furanic compound 2FOL of 67ppb was detected which indicates the solid insulation is wet. It is important to maintain the oil in a good condition so as not to further deteriorate the paper insulation.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factors at 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.02% by weight is detected, thus UNACCEPTABLE.

Insufficient oil inhibitor will cause the insulating oil to oxidize at a faster rate, thus degrading the paper insulation.

- Corrosive sulfur test on copper strip resultant in dark orange, thus Noncorrosive of 1B.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 7 of 25

#### Ref No : TXM/MKT-1200/SA/CI17049

B) Recommendation

- It is recommended to perform Transformer Oil Regeneration on this unit. Transformer oil regeneration at this stage of contamination will effectively remove unwanted oxidation byproducts as well as moisture from the insulating oil. This process will restore the oil back to its original quality, thus protecting the paper insulation and extending the transformer serviceable lifespan. Furthermore, oil inhibitor 2,6-DBPC and passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 8 of 25

### CENNIX LABORATORY (M) SDN BHD	     6

#### (Formerly known as Myers-Musteq Sdn Bhd)

|  |  |  |  |  | VISUAL INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | STATUS OIL TEMP °C |  | W. TEMP °C |  | OIL LEVEL |  | PAINT |  | S. GEL |  | LEAKS |  |  |
| 04/07/2017 |  | 37 |  |  | NORMAL |  |  |  | GOOD |  |  |  |  |
| 31/07/2017 | OFFLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 30/08/2017 | OFFLINE | 39 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 29/09/2017 | OFFLINE | 40 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 30/10/2017 | OFFLINE | 44 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 27/11/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 06/12/2017 | OFFLINE |  |  |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |  |  |
|  |  | ASTM D974 |  |  |  |  |  |  |  |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
|  |  |  |  | ASTM D971 |  | IEC 156 |  | ASTM D1500 |  |  |  |  |  |
| DATE | SERVICES | ACID |  | IFT |  | DIEL |  | COLOUR |  |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) |  | (kV) |  |  |  |  |  |  |  |
| 04/07/2017 | ROUTINE | 0.042 AC |  | 26.6 UN |  | 41 AC |  | 1.5 AC |  |  | 0.8540 AC | CLEAR AC |  |
| 31/07/2017 | ROUTINE | 0.045 AC |  |  |  | 25 QU |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/08/2017 | ROUTINE | 0.042 AC |  |  |  | 42 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 29/09/2017 | ROUTINE | 0.048 AC |  |  |  | 59 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/10/2017 | ROUTINE | 0.051 QU |  |  |  | 62 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 27/11/2017 | ROUTINE | 0.051 QU |  |  |  | 50 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 06/12/2017 | ROUTINE | 0.053 QU |  | 27.3 UN |  | 51 AC |  | 1.5 AC |  |  | 0.8589 AC | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	27	18639	66781	3	64	1106	ND	1	ND	95	86621

06/12/2017	20	19360	61590	3	45	728	ND	1	ND	69	81747

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	27	21	2.48	D 31/07/2017	24	27	3.91	E

30/08/2017	28	14	1.65	C

29/09/2017	31	19	1.80	D

30/10/2017	35	17	1.21	B

27/11/2017	35	18	1.28	B 06/12/2017	30	17	1.78	D

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 2 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - FUJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 10035

KVA	 -

PRI	 - 72000 V

SEC	 - 380 V

KILOGRAMS	 - 1000

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 630

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

###### DATE	SERVICE

CENNIX LABORATORY SDN BHD 6 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | 62 | ND | ND | ND | 62 |
| 06/12/2017 | ND | 67 | ND | ND | ND | 67 |

RECOMMENDATION:

FURAN ANALYSIS SHOWS DETECTION OF 2FOL WHICH INDICATES THAT THE SOLID INSULATION IS

WET. IT IS ADVISABLE TO MAINTAIN THE OIL IN A GOOD CONDITION SO AS NOT TO FURTHER DETERIORATE THE PAPER INSULATION.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  ND	  0.01	  ND

06/12/2017	  ND	  ND	  0.02

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	1.900 AC	04/07/2017	0.02 UN

06/12/2017	0.000 AC	 	0.980 AC	06/12/2017	0.02 UN

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	1A	LIGHT ORANGE

06/12/2017	NON-COR	1B	DARK ORANGE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 2 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - FUJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 10035

KVA	 -

PRI	 - 72000 V

SEC	 - 380 V

KILOGRAMS	 - 1000

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 630

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 4. | TRAFO 3 ESP UNIT 1 | 10031 | 7 |

A) Analysis

- Acidity of 0.053mgKOH/gm and IFT of 28.3mN/m are QUESTIONABLE. These two parameters indicates there are formation of oxidation by products in the oil. Close monitoring is advised.

- Dielectric of 57kV is ACCEPTABLE.

- Colour, Specific Gravity, and Visualization for the oil are within the ACCEPTABLE range.

- DGA indicates the transformer is operating satisfactorily, without significant amount of combustible gases being generated.

- Water content in oil of 16ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.68% M/dw is graded as C. For this transformer, it is advisable to maintain the water content level below 20ppm.

- Furanic compound 2FOL of 14ppb was detected which indicates the solid insulation is wet. It is important to maintain the oil in a good condition so as not to further deteriorate the paper insulation.

- Metals-In-Oil were not detected, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.01% by weight is detected, thus UNACCEPTABLE.

Insufficient oil inhibitor will cause the insulating oil to oxidize at a faster rate, thus degrading the paper insulation.

- Tested on copper strip resultant in multicolored with lavender blue and/or silver overlaid on claret red, thus Non-corrosive of 2C.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 9 of 25

#### Ref No : TXM/MKT-1200/SA/CI17049

B) Recommendation

- Retest Acidity and Interfacial Tension in 6 months to assess if the insulating oil deteriorate to a level that require corrective action to improve the oil quality.

- It is recommended to add oil inhibitor (2,6-DBPC) until the acceptance level (IEEE Std 57-106 suggests 0.09% as minimum level) as soon as possible so as to retard oil oxidation process. By doing so, oil degradation will be slowed down, hence protecting and preserving the transformer insulating material.

- Add passivator before the sulfur convert to be corrosive enough to attack copper. Passivator would coat the copper surface to retard or delay attack by corrosive sulfur.

- Other parameters: Do carry-out *Liquid Screen, Liquid Power Factor, Inhibitor, Water Content, Metals-In-Oil, Furan Analysis & DGA periodically for Condition Monitoring purposes

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 10 of 25

### CENNIX LABORATORY (M) SDN BHD	     7

#### (Formerly known as Myers-Musteq Sdn Bhd)

|  |  |  |  |  | VISUAL INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | STATUS OIL TEMP °C |  | W. TEMP °C |  | OIL LEVEL |  | PAINT |  | S. GEL |  | LEAKS |  |  |
| 04/07/2017 |  | 28 |  |  | NORMAL |  |  |  | GOOD |  |  |  |  |
| 31/07/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 30/08/2017 | OFFLINE | 35 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 29/09/2017 | OFFLINE | 38 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 30/10/2017 | OFFLINE | 44 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 27/11/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 06/12/2017 | OFFLINE |  |  |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |  |  |
|  |  | ASTM D974 |  |  |  |  |  |  |  |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
|  |  |  |  | ASTM D971 |  | IEC 156 |  | ASTM D1500 |  |  |  |  |  |
| DATE | SERVICES | ACID |  | IFT |  | DIEL |  | COLOUR |  |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) |  | (kV) |  |  |  |  |  |  |  |
| 04/07/2017 | ROUTINE | 0.048 AC |  | 28.4 QU |  | 44 AC |  | 1.0 AC |  |  | 0.8537 AC | CLEAR AC |  |
| 31/07/2017 | ROUTINE | 0.042 AC |  |  |  | 77 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/08/2017 | ROUTINE | 0.042 AC |  |  |  | 61 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 29/09/2017 | ROUTINE | 0.045 AC |  |  |  | 72 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/10/2017 | ROUTINE | 0.048 AC |  |  |  | 72 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 27/11/2017 | ROUTINE | 0.051 QU |  |  |  | 62 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 06/12/2017 | ROUTINE | 0.053 QU |  | 28.3 QU |  | 57 AC |  | 1.5 AC |  |  | 0.8624 AC | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	32	15273	65111	5	95	1002	ND	2	ND	134	81520

06/12/2017	7	14730	65738	3	42	617	ND	ND	ND	52	81137

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	25	32	4.16	E

31/07/2017	25	16	2.08	D

30/08/2017	30	13	1.37	C

29/09/2017	32	14	1.33	B

30/10/2017	37	16	1.04	B

27/11/2017	34	17	1.39	C

06/12/2017	30	16	1.68	C

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 3 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - FUJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 10031

KVA	 -

PRI	 - 72000 V

SEC	 - 380 V

KILOGRAMS	 - 1000

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 630

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

###### DATE	SERVICE

CENNIX LABORATORY SDN BHD 7 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

DATE	5H2F	2FOL	2FAL	2ACF	5M2F	TOTAL

04/07/2017	 ND	 32	 ND	 ND	 ND	 32

06/12/2017	 ND	 14	 ND	 ND	 ND	 14

RECOMMENDATION:

FURAN ANALYSIS SHOWS DETECTION OF 2FOL WHICH INDICATES THAT THE SOLID INSULATION IS

WET. IT IS ADVISABLE TO MAINTAIN THE OIL IN A GOOD CONDITION SO AS NOT TO FURTHER DETERIORATE THE PAPER INSULATION.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  0.01	  0.01	  0.01

06/12/2017	  ND	  ND	  ND

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	1.700 AC	04/07/2017	0.01 UN

06/12/2017	0.000 AC	 	0.630 AC	06/12/2017	0.01 UN

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	1A	LIGHT ORANGE

06/12/2017	NON-COR	2C	LAVENDER BLUE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 3 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - FUJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 10031

KVA	 -

PRI	 - 72000 V

SEC	 - 380 V

KILOGRAMS	 - 1000

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 630

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 5. | TRAFO 4 ESP UNIT 1 | 10034 | 8 |

A) Analysis

- Acidity of 0.031mgKOH/g is ACCEPTABLE while IFT of 27.2mN/m is UNACCEPTABLE. The low IFT level indicates the oil is containing contaminants that had weakened the Interfacial tension of the oil.

Removal of these contaminations is highly recommended.

- Dielectric of 41kV is ACCEPTABLE.

- Colour, Specific Gravity, and Visualization for the oil are within the ACCEPTABLE range.

- DGA indicates the transformer is operating satisfactorily, without significant amount of combustible gases being generated.

- Water content in oil of 18ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.89% M/dw is graded as D. The value is approaching the borderline of questionable level. For this transformer, it is advisable to maintain the water content level below 20ppm.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factor for 25°C and 100°C are ACCEPTABLE.

- Oil Inhibitor of 0.06% by weight is detected, thus UNACCEPTABLE.

Insufficient oil inhibitor will cause the insulating oil to oxidize at a faster rate, thus degrading the paper insulation.

- Tested on copper strip resultant in multicolored with lavender blue and/or silver overlaid on claret red, thus Non-corrosive of 2C.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 11 of 25

#### Ref No : TXM/MKT-1200/SA/CI17049

B) Recommendation

- It is recommended to perform Transformer Oil Regeneration on this unit. Transformer oil regeneration at this stage of contamination will effectively remove unwanted oxidation byproducts as well as moisture from the insulating oil. This process will restore the oil back to its original quality, thus protecting the paper insulation and extending the transformer serviceable lifespan. Furthermore, oil inhibitor 2,6-DBPC and passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 12 of 25

### CENNIX LABORATORY (M) SDN BHD	     8

#### (Formerly known as Myers-Musteq Sdn Bhd)

|  |  |  |  |  | VISUAL INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | STATUS OIL TEMP °C |  | W. TEMP °C |  | OIL LEVEL |  | PAINT |  | S. GEL |  | LEAKS |  |  |
| 04/07/2017 |  | 28 |  |  | NORMAL |  |  |  | BAD |  |  |  |  |
| 31/07/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 30/08/2017 | OFFLINE | 34 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 29/09/2017 | OFFLINE | 40 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 30/10/2017 | OFFLINE | 44 |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 27/11/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 06/12/2017 | OFFLINE |  |  |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |  |  |
|  |  | ASTM D974 |  |  |  |  |  |  |  |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
|  |  |  |  | ASTM D971 |  | IEC 156 |  | ASTM D1500 |  |  |  |  |  |
| DATE | SERVICES | ACID |  | IFT |  | DIEL |  | COLOUR |  |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) |  | (kV) |  |  |  |  |  |  |  |
| 04/07/2017 | ROUTINE | 0.028 AC |  | 26.3 UN |  | 24 UN |  | 1.5 AC |  |  | 0.8596 AC | CLEAR AC |  |
| 31/07/2017 | ROUTINE | 0.022 AC |  |  |  | 88 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/08/2017 | ROUTINE | 0.028 AC |  |  |  | 44 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 29/09/2017 | ROUTINE | 0.031 AC |  |  |  | 53 AC |  | 1.0 AC |  |  |  | CLEAR AC |  |
| 30/10/2017 | ROUTINE | 0.028 AC |  |  |  | 48 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 27/11/2017 | ROUTINE | 0.034 AC |  |  |  | 41 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 06/12/2017 | ROUTINE | 0.031 AC |  | 27.2 UN |  | 41 AC |  | 1.5 AC |  |  | 0.8645 AC | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	13	12265	66770	5	172	1206	ND	8	ND	198	80439

06/12/2017	8	13331	63527	3	70	720	ND	1	ND	82	77660

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	26	29	3.77	E

31/07/2017	26	15	1.95	D

30/08/2017	30	13	1.37	C

29/09/2017	33	15	1.23	B

30/10/2017	39	18	0.99	B

27/11/2017	37	30	1.95	D

06/12/2017	30	18	1.89	D

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 4 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - FUJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 10034

KVA	 -

PRI	 - 72000 V

SEC	 - 380 V

KILOGRAMS	 - 1000

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 630

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

###### DATE	SERVICE

CENNIX LABORATORY SDN BHD 8 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

DATE	5H2F	2FOL	2FAL	2ACF	5M2F	TOTAL

04/07/2017	 ND	 18	 ND	 ND	 ND	 18

06/12/2017	 ND	 ND	 ND	 ND	 ND	 ND

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  0.05	  0.02	  0.01

06/12/2017	  ND	  ND	  0.02

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.180 QU	 	6.680 UN	04/07/2017	0.08 UN

06/12/2017	0.010 AC	 	2.180 AC	06/12/2017	0.06 UN

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	2C	LAVENDER BLUE 06/12/2017	NON-COR	2C	LAVENDER BLUE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 4 ESP UNIT 1

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - FUJIAN

DATE MFG	 - 2010

MAIN TANK S/N	 - 10034

KVA	 -

PRI	 - 72000 V

SEC	 - 380 V

KILOGRAMS	 - 1000

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 -

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 630

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 6. | MAIN TRAFO UNIT 3 | 1122170 | 9 |

A) Analysis

- Acidity of 0.014mgKOH/g and IFT of 41.5mN/m are ACCEPTABLE.

- Dielectric of 84kV is ACCEPTABLE.

- Specific gravity, Colour, and Visualization of oil is in the ACCEPTABLE range.

- The DGA result shows that Carbon Monoxide to have stabilized. Other gases remain within normal limits and does not indicate any fault afflicting the transformer unit. Proceed with annual monitoring.

- Water Content in oil of 9ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 0.58% M/dw is graded as A. For this transformer, it is recommended to maintain water content in oil at less than 20ppm.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.22% by weight is detected, thus ACCEPTABLE.

- Tested on copper strip resultant in multicolored with lavender blue and/or silver overlaid on claret red, thus Non-corrosive of 2C.

B) Recommendation

- Add passivator before the sulfur convert to be corrosive enough to attack copper. Passivator would coat the copper surface to retard or delay attack by corrosive sulfur.

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 13 of 25

### CENNIX LABORATORY (M) SDN BHD	     9

#### (Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE	STATUS	OIL TEMP °C	W. TEMP °C	OIL LEVEL	PAINT	S. GEL	LEAKS

04/07/2017	ONLINE	46	56	GOOD

31/07/2017	ONLINE	48	50

30/08/2017	ONLINE	55	60	NORMAL	FAIR	GOOD	NONE

29/09/2017	ONLINE	58	68	NORMAL	FAIR	GOOD	NONE

30/10/2017	OFFLINE	32	32	NORMAL	FAIR	GOOD	NONE

27/11/2017	ONLINE	46	50

06/12/2017	ONLINE	57	48

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

04/07/2017	ROUTINE	    0.017 AC	42.3 AC	78 AC	   0.5 AC	     	0.8780 AC	CLEAR AC

31/07/2017	ROUTINE	    0.014 AC	 	77 AC	   0.5 AC	     	 	CLEAR AC

30/08/2017	ROUTINE	    0.017 AC	 	86 AC	   0.5 AC	     	 	CLEAR AC

29/09/2017	ROUTINE	    0.014 AC	 	86 AC	   0.5 AC	     	 	CLEAR AC

30/10/2017	ROUTINE	    0.014 AC	 	88 AC	   0.5 AC	     	 	CLEAR AC

27/11/2017	ROUTINE	    0.014 AC	 	87 AC	   0.5 AC	     	 	CLEAR AC

06/12/2017	ROUTINE	    0.014 AC	41.5 AC	84 AC	   0.5 AC	     	0.8832 AC	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	24	10131	44084	11	641	2250	1	1	ND	678	57143

06/12/2017	39	14023	43226	11	668	2456	ND	1	ND	719	60424

RECOMMENDATION:

GAS LEVELS HAVE REMAINED STABLE. PROCEED WITH ANNUAL MONITORING.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	33	15	1.23	B

31/07/2017	35	17	1.21	B

30/08/2017	35	8	0.57	A

29/09/2017	42	10	0.50	A

30/10/2017	28	9	1.06	B

27/11/2017	35	8	0.57	A

06/12/2017	37	9	0.58	A

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - MAIN TRAFO UNIT 3

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - SHANDONG

DATE MFG	 - 2010

MAIN TANK S/N	 - 1122170

KVA	 - 40000

PRI	 - 165000 V

SEC	 - 6300 V

KILOGRAMS	 - 73920

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAF

IMPEDENCE	 - 13.79%

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 26708

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - YES H2O COOLED	 - NO OIL PUMPS	 - YES TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - YES BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

###### DATE	SERVICE

CENNIX LABORATORY SDN BHD 9 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | ND | ND | ND | ND |
| 06/12/2017 | ND | ND | ND | ND | ND | ND |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  0.01	  0.01	  0.02

06/12/2017	  0.01	  ND	  0.03

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	0.130 AC	04/07/2017	0.22 AC

06/12/2017	0.000 AC	 	0.070 AC	06/12/2017	0.22 AC

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	3A	MAGENTA

06/12/2017	NON-COR	2C	LAVENDER BLUE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - MAIN TRAFO UNIT 3

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

MFG	 - SHANDONG

DATE MFG	 - 2010

MAIN TANK S/N	 - 1122170

KVA	 - 40000

PRI	 - 165000 V

SEC	 - 6300 V

KILOGRAMS	 - 73920

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAF

IMPEDENCE	 - 13.79%

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 26708

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - YES H2O COOLED	 - NO OIL PUMPS	 - YES TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - YES BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 7. | UAT 3 | 1035082 | 10 |

- A) Analysis Acidity of 0.020mgKOH/g and IFT of 37.6mN/m are ACCEPTABLE.

- Dielectric of 86kV is ACCEPTABLE.

- Specific gravity, Colour, and Visualization of oil is in the ACCEPTABLE range.

- Dissolved Gas Analysis reveals further increases in Carbon Monoxide and Dioxide while other gases remain within normal limits. As the amount is significantly high, transformer manufacturer can be consulted for the similar cases with the same design of the transformer. Meanwhile, proceed with annual monitoring.

- Water Content in oil of 12ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 0.66% M/dw is graded as A. For this transformer, it is recommended to maintain water content in oil at less than 30ppm.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.23% by weight is detected, thus ACCEPTABLE.

Tested on copper strip resultant in multicolored with lavender blue a

- nd/or silver overlaid on claret red, thus Non-corrosive of 2C.

B) Recommendation

- Add passivator before the sulfur convert to be corrosive enough to attack copper. Passivator would coat the copper surface to retard or delay attack by corrosive sulfur.

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 14 of 25

### CENNIX LABORATORY (M) SDN BHD	     10

#### (Formerly known as Myers-Musteq Sdn Bhd)

|  |  |  |  |  | VISUAL INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | STATUS OIL TEMP °C |  | W. TEMP °C |  | OIL LEVEL |  | PAINT |  | S. GEL |  | LEAKS |  |  |
| 04/07/2017 | ONLINE |  | 55 |  |  |  |  |  | BAD |  |  |  |  |
| 31/07/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 30/08/2017 | ONLINE |  | 58 |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 29/09/2017 | ONLINE |  | 58 |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 30/10/2017 | OFFLINE |  | 44 |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 27/11/2017 | ONLINE |  | 60 |  |  |  |  |  |  |  |  |  |  |
| 06/12/2017 | ONLINE |  | 60 |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |  |  |
|  |  | ASTM D974 |  |  |  |  |  |  |  |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
|  |  |  |  | ASTM D971 |  | IEC 156 |  | ASTM D1500 |  |  |  |  |  |
| DATE | SERVICES | ACID |  | IFT |  | DIEL |  | COLOUR |  |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) |  | (kV) |  |  |  |  |  |  |  |
| 04/07/2017 | ROUTINE | 0.022 AC |  | 38.1 AC |  | 60 AC |  | 0.5 AC |  |  | 0.8767 AC | CLEAR AC |  |
| 31/07/2017 | ROUTINE | 0.025 AC |  |  |  | 88 AC |  | 0.5 AC |  |  |  | CLEAR AC |  |
| 30/08/2017 | ROUTINE | 0.022 AC |  |  |  | 89 AC |  | 0.5 AC |  |  |  | CLEAR AC |  |
| 29/09/2017 | ROUTINE | 0.020 AC |  |  |  | 80 AC |  | 0.5 AC |  |  |  | CLEAR AC |  |
| 30/10/2017 | ROUTINE | 0.022 AC |  |  |  | 86 AC |  | 0.5 AC |  |  |  | CLEAR AC |  |
| 27/11/2017 | ROUTINE | 0.022 AC |  |  |  | 86 AC |  | 0.5 AC |  |  |  | CLEAR AC |  |
| 06/12/2017 | ROUTINE | 0.020 AC |  | 37.6 AC |  | 86 AC |  | 0.5 AC |  |  | 0.8820 AC | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

| 04/07/2017 | 20 | 16028 | 68308 | 20 | 971 | 3536 | 5 | 7 | ND | 1023 | 88895 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 06/12/2017 | 36 | 18752 | 66758 | 19 | 1116 | 3622 | 5 | 7 | ND | 1183 | 90315 |

RECOMMENDATION:

CARBON MONOXIDE AND CARBON DIOXIDE LEVEL ARE HIGH. OTHER GASES LEVELS ARE ASSESSED AS ACCEPTABLE.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

| DATE | TEMP°C | PPM | %M/dw | GRADE |
| --- | --- | --- | --- | --- |
| 04/07/2017 | 33 | 11 | 0.90 | A |
| 31/07/2017 | 32 | 14 | 1.33 | B |
| 30/08/2017 | 35 | 11 | 0.78 | A |
| 29/09/2017 | 37 | 12 | 0.78 | A |
| 30/10/2017 | 29 | 11 | 1.15 | A |
| 27/11/2017 | 37 | 12 | 0.78 | A |
| 06/12/2017 | 39 | 12 | 0.66 | A |

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK UNIT# - UAT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

MFG	 - SHANDONG

DATE MFG	 - 2010

MAIN TANK S/N	 - 1035082

KVA	 - 6300

PRI	 - 6300 V

SEC	 - 6300 V

KILOGRAMS	 - 14600

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 - 5.78%

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 3749

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

##### DATE	SERVICE

CENNIX LABORATORY SDN BHD 10 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | ND | ND | ND | ND |
| 06/12/2017 | ND | ND | ND | ND | ND | ND |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  0.02	  0.01	  0.04

06/12/2017	  ND	  0.01	  0.08

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	0.390 AC	04/07/2017	0.23 AC

06/12/2017	0.000 AC	 	0.170 AC	06/12/2017	0.23 AC

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	3A	MAGENTA

06/12/2017	NON-COR	2C	LAVENDER BLUE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK UNIT# - UAT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

MFG	 - SHANDONG

DATE MFG	 - 2010

MAIN TANK S/N	 - 1035082

KVA	 - 6300

PRI	 - 6300 V

SEC	 - 6300 V

KILOGRAMS	 - 14600

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 - 5.78%

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 3749

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 8. | TRAFO 1 ESP UNIT 3 | 007308428 | 11 |

A) Analysis

- Acidity of 0.022mgKOH/g and IFT of 34.6mN/m are ACCEPTABLE.

- Dielectric of 31kV is ACCEPTABLE.

- Colour and Visualization for the oil are within the ACCEPTABLE range.

- Specific Gravity value is inside the QUESTIONABLE range. Close monitoring is needed and the cause should be identified.

- DGA indicates the transformer is operating satisfactorily, without significant amount of combustible gases being generated.

- Water content in oil of 31ppm is UNACCEPTABLE. Meanwhile Water Content in solid insulation of 1.39% M/dw is graded as C. For this transformer, it is advisable to maintain the water content level below 30ppm. This indicates the presence of high water content in the oil. The presence of high water content could cause dielectric failure.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.18% by weight is detected, thus QUESTIONABLE.

Insufficient oil inhibitor will cause the insulating oil to oxidize at a faster rate, thus degrading the paper insulation.

- Corrosive sulfur test on copper strip resultant in colour changes to brassy and gold, thus Non-corrosive of 2E.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 15 of 25

#### Ref No : TXM/MKT-1200/SA/CI17049

B) Recommendation

- The Specific Gravity of the oil needs further investigation. Should the unit is safe to operate with the current oil-filled, highly recommended to perform OIL PURIFICATION. Result indicates that the moisture content in the transformer oil is not conducive for normal operation of a transformer. Oil purification will remove excessive moisture detected in the transformer oil and thus improving dielectric breakdown voltage of the mineral oil. Furthermore, oil inhibitor 2,6-DBPC and passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 16 of 25

### CENNIX LABORATORY (M) SDN BHD	     11

#### (Formerly known as Myers-Musteq Sdn Bhd)

|  |  |  |  |  | VISUAL INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | STATUS OIL TEMP °C |  | W. TEMP °C |  | OIL LEVEL |  | PAINT |  | S. GEL |  | LEAKS |  |  |
| 31/07/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 30/08/2017 | ONLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 29/09/2017 | ONLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 30/10/2017 | OFFLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 28/11/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 06/12/2017 | ONLINE |  |  |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |  |  |
|  |  | ASTM D974 |  |  |  |  |  |  |  |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
|  |  |  |  | ASTM D971 |  | IEC 156 |  | ASTM D1500 |  |  |  |  |  |
| DATE | SERVICES | ACID |  | IFT |  | DIEL |  | COLOUR |  |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) |  | (kV) |  |  |  |  |  |  |  |
| 04/07/2017 | ROUTINE | 0.022 AC |  | 23.2 UN |  | 32 AC |  | 1.5 AC |  |  | 0.8432 AC | CLEAR AC |  |
| 31/07/2017 | ROUTINE | 0.028 AC |  |  |  | 47 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/08/2017 | ROUTINE | 0.028 AC |  |  |  | 36 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 29/09/2017 | ROUTINE | 0.025 AC |  |  |  | 45 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/10/2017 | ROUTINE | 0.025 AC |  |  |  | 40 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 28/11/2017 | ROUTINE | 0.025 AC |  |  |  | 31 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 06/12/2017 | ROUTINE | 0.022 AC |  | 34.6 AC |  | 31 AC |  | 1.5 AC |  |  | 0.8180 QU | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	14	12943	68807	3	62	1243	ND	ND	ND	79	83072

06/12/2017	14	12739	65097	3	66	612	ND	ND	ND	83	78531

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	36	26	1.85	D

31/07/2017	31	21	2.00	D

30/08/2017	30	22	2.31	D

29/09/2017	34	20	1.64	C

30/10/2017	28	19	2.24	D

28/11/2017	43	34	1.53	C

06/12/2017	43	31	1.39	C

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 1 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0073084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 416 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - NO CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

###### DATE	SERVICE

CENNIX LABORATORY SDN BHD 11 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | ND | ND | ND | ND |
| 06/12/2017 | ND | ND | ND | ND | ND | ND |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  0.01	  0.01	  ND

06/12/2017	  0.01	  ND	  ND

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	0.350 AC	04/07/2017	ND UN

06/12/2017	0.000 AC	 	0.040 AC	06/12/2017	0.18 QU

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	1B	DARK ORANGE

06/12/2017	NON-COR	2E	BRASSY GOLD

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 1 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0073084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 416 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - NO CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 9. | TRAFO 2 ESP UNIT 3 | 0070084208 | 12 |

A) Analysis

- Acidity of 0.22mgKOH/g is ACCEPTABLE while IFT of 29.7mN/m is QUESTIONABLE. This indicates the presence of oxidation by products in the oil.

- Dielectric of 29kV is QUESTIONABLE. This is reflected from the high moisture content detected in the transformer oil.

- Colour and Visualization for the oil are within the ACCEPTABLE range.

- Specific Gravity value is inside the QUESTIONABLE range. Close monitoring is needed and the cause should be identified.

- DGA indicates the transformer is operating satisfactorily, without significant amount of combustible gases being generated.

- Water Content in oil of 44ppm is UNACCEPTABLE. Meanwhile Water Content in solid insulation of 1.98% M/dw is graded as D. For this transformer, it is recommended to maintain water content in oil at less than 20ppm. This indicates the presence of high water content in the oil. The presence of high water content could cause dielectric failure.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil were not detected, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.20% by weight is detected, thus ACCEPTABLE.

- Tested on copper strip resultant in magenta overcoat on brassy strip, thus Non-corrosive of 3A.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 17 of 25

#### Ref No : TXM/MKT-1200/SA/CI17049

B) Recommendation

- The Specific Gravity of the oil needs further investigation. Should the unit is safe to operate with the current oil-filled, highly recommended to perform OIL Regeneration. Transformer oil regeneration at this stage of contamination will effectively remove unwanted oxidation byproducts as well as excess moisture from the insulating oil. This process will restore the oil back to its original quality, thus protecting the paper insulation and extending the transformer serviceable lifespan. Furthermore, passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 18 of 25

### CENNIX LABORATORY (M) SDN BHD	     12

#### (Formerly known as Myers-Musteq Sdn Bhd)

|  |  |  |  |  | VISUAL INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | STATUS OIL TEMP °C |  | W. TEMP °C |  | OIL LEVEL |  | PAINT |  | S. GEL |  | LEAKS |  |  |
| 30/08/2017 | OFFLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 29/09/2017 | ONLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 30/10/2017 | OFFLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 28/11/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 06/12/2017 | ONLINE |  |  |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |  |  |
|  |  | ASTM D974 |  |  |  |  |  |  |  |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
|  |  |  |  | ASTM D971 |  | IEC 156 |  | ASTM D1500 |  |  |  |  |  |
| DATE | SERVICES | ACID |  | IFT |  | DIEL |  | COLOUR |  |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) |  | (kV) |  |  |  |  |  |  |  |
| 04/07/2017 | ROUTINE | 0.118 UN |  | 16.2 UN |  | 24 UN |  | 3.0 AC |  |  | 0.8435 AC | CLEAR AC |  |
| 31/07/2017 | ROUTINE | 0.112 UN |  |  |  | 28 QU |  | 3.0 AC |  |  |  | CLEAR AC |  |
| 30/08/2017 | ROUTINE | 0.109 UN |  |  |  | 34 AC |  | 2.5 AC |  |  |  | CLEAR AC |  |
| 29/09/2017 | ROUTINE | 0.115 UN |  |  |  | 21 UN |  | 2.5 AC |  |  |  | CLEAR AC |  |
| 30/10/2017 | ROUTINE | 0.118 UN |  |  |  | 33 AC |  | 2.5 AC |  |  |  | CLEAR AC |  |
| 28/11/2017 | ROUTINE | 0.017 AC |  |  |  | 25 QU |  | 0.5 AC |  |  |  | CLEAR AC |  |
| 06/12/2017 | ROUTINE | 0.022 AC |  | 29.7 QU |  | 29 QU |  | 0.5 AC |  |  | 0.8106 QU | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	38	16781	70523	5	129	2431	3	5	ND	180	89915

06/12/2017	42	19523	66059	3	102	912	ND	ND	ND	147	86641

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	37	39	2.54	D 31/07/2017	31	38	3.61	E

30/08/2017	26	17	2.21	D

29/09/2017	36	37	2.63	D

30/10/2017	28	20	2.36	D 28/11/2017	43	28	1.26	B 06/12/2017	43	44	1.98	D

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 2 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0070084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 415 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

###### DATE	SERVICE

CENNIX LABORATORY SDN BHD 12 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | 169 | ND | ND | 169 |
| 06/12/2017 | ND | ND | ND | ND | ND | ND |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  ND	  0.01	  0.01

06/12/2017	  ND	  ND	  ND

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	1.330 AC	04/07/2017	ND UN

06/12/2017	0.000 AC	 	0.030 AC	06/12/2017	0.20 AC

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	2C	LAVENDER BLUE

06/12/2017	NON-COR	3A	MAGENTA

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 2 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0070084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 415 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 10. | TRAFO 3 ESP UNIT 3 | 0072084208 | 13 |

A) Analysis

- Acidity of 0.014mgKOH/g and IFT of 39.8mN/m are ACCEPTABLE.

- Dielectric of 45kV is ACCEPTABLE.

- Colour and Visualization for the oil are within the ACCEPTABLE range.

- Specific Gravity value is inside the QUESTIONABLE range. Close monitoring is needed and the cause should be identified.

- DGA indicates the transformer is operating satisfactorily, without significant amount of combustible gases being generated.

- Water content in oil of 29ppm is UNACCEPTABLE. Meanwhile Water Content in solid insulation of 1.30% M/dw is graded as B. For this transformer, it is advisable to maintain the water content level below 20ppm. This indicates the presence of high water content in the oil. The presence of high water content could cause dielectric failure.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil were not detected, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.21% by weight is detected, thus ACCEPTABLE.

- Corrosive sulfur test on copper strip resultant in colour changes to brassy and gold, thus Non-corrosive of 2E.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 19 of 25

#### Ref No : TXM/MKT-1200/SA/CI17049

B) Recommendation

- The Specific Gravity of the oil needs further investigation. Should the unit is safe to operate with the current oil-filled, highly recommended to perform OIL PURIFICATION. Result indicates that the moisture content in the transformer oil is not conducive for normal operation of a transformer. Oil purification will remove excessive moisture detected in the transformer oil and thus improving dielectric breakdown voltage of the mineral oil. Furthermore, passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 20 of 25

### CENNIX LABORATORY (M) SDN BHD	     13

#### (Formerly known as Myers-Musteq Sdn Bhd)

|  |  |  |  |  | VISUAL INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | STATUS OIL TEMP °C |  | W. TEMP °C |  | OIL LEVEL |  | PAINT |  | S. GEL |  | LEAKS |  |  |
| 04/07/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 31/07/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 30/08/2017 | ONLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 29/09/2017 | ONLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 30/10/2017 | OFFLINE |  |  |  | LOW |  | FAIR |  | GOOD |  | NONE |  |  |
| 28/11/2017 | ONLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 06/12/2017 | ONLINE |  |  |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |  |  |
|  |  | ASTM D974 |  |  |  |  |  |  |  |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
|  |  |  |  | ASTM D971 |  | IEC 156 |  | ASTM D1500 |  |  |  |  |  |
| DATE | SERVICES | ACID |  | IFT |  | DIEL |  | COLOUR |  |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) |  | (kV) |  |  |  |  |  |  |  |
| 04/07/2017 | ROUTINE | 0.025 AC |  | 27.8 UN |  | 40 AC |  | 1.5 AC |  |  | 0.8415 AC | CLEAR AC |  |
| 31/07/2017 | ROUTINE | 0.025 AC |  |  |  | 66 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/08/2017 | ROUTINE | 0.025 AC |  |  |  | 50 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 29/09/2017 | ROUTINE | 0.028 AC |  |  |  | 59 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 30/10/2017 | ROUTINE | 0.028 AC |  |  |  | 55 AC |  | 1.5 AC |  |  |  | CLEAR AC |  |
| 28/11/2017 | ROUTINE | 0.014 AC |  |  |  | 39 AC |  | 0.5 AC |  |  |  | CLEAR AC |  |
| 06/12/2017 | ROUTINE | 0.014 AC |  | 39.8 AC |  | 45 AC |  | 0.5 AC |  |  | 0.8099 QU | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	21	16364	70694	3	38	1068	ND	ND	ND	62	88188

06/12/2017	15	14515	65277	2	40	559	ND	ND	ND	57	80408

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	37	27	1.75	D

31/07/2017	29	18	1.89	D

30/08/2017	35	21	1.49	C

29/09/2017	37	22	1.43	C

30/10/2017	28	16	1.89	D

28/11/2017	44	24	1.08	B

06/12/2017	44	29	1.30	B

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 3 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0072084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 415 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

###### DATE	SERVICE

CENNIX LABORATORY SDN BHD 13 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | ND | ND | ND | ND |
| 06/12/2017 | ND | ND | ND | ND | ND | ND |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  ND	  0.01	  ND

06/12/2017	  ND	  ND	  ND

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	0.620 AC	04/07/2017	0.01 UN

06/12/2017	0.000 AC	 	0.080 AC	06/12/2017	0.21 AC

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	2C	LAVENDER BLUE

06/12/2017	NON-COR	2E	BRASSY GOLD

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK

##### UNIT# - TRAFO 3 ESP UNIT 3

LOCATION - OUTDOOR OTHER -

###### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0072084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 415 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 11. | TRAFO 4 UNIT 3 | 0071084208 | 14 |

A) Analysis

- Acidity of 0.25mgKOH/g is ACCEPTABLE while IFT of 29.8mN/m is QUESTIONABLE. This indicates the presence of oxidation by products in the oil.

- Dielectric of 43kV is ACCEPTABLE.

- Colour, Specific Gravity, and Visualization for the oil are within the ACCEPTABLE range.

- DGA indicates the transformer is operating satisfactorily, without significant amount of combustible gases being generated.

- Water content in oil of 19ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.80% M/dw is graded as D. For this transformer, it is advisable to maintain the water content level below 20ppm.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.03% by weight is detected, thus UNACCEPTABLE.

Insufficient oil inhibitor will cause the insulating oil to oxidize at a faster rate, thus degrading the paper insulation.

- Corrosive sulfur test on copper strip resultant in dark orange, thus Noncorrosive of 1B.

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 21 of 25

#### Ref No : TXM/MKT-1200/SA/CI17049

B) Recommendation

- Retest Acidity and Interfacial Tension in 6 months to assess if the insulating oil deteriorate to a level that require corrective action to improve the oil quality

- It is recommended to add oil inhibitor (2,6-DBPC) until the acceptance level (IEEE Std 57-106 suggests 0.09% as minimum level) as soon as possible so as to retard oil oxidation process. By doing so, oil degradation will be slowed down, hence protecting and preserving the transformer insulating material.

- Add passivator before the sulfur convert to be corrosive enough to attack copper. Passivator would coat the copper surface to retard or delay attack by corrosive sulfur.

- Other parameters: Do carry-out *Liquid Screen, Liquid Power Factor, Inhibitor, Water Content, Metals-In-Oil, Furan Analysis & DGA periodically for Condition Monitoring purposes

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 22 of 25

### CENNIX LABORATORY (M) SDN BHD	     14

#### (Formerly known as Myers-Musteq Sdn Bhd)

|  |  |  |  |  | VISUAL INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | STATUS OIL TEMP °C |  | W. TEMP °C |  | OIL LEVEL |  | PAINT |  | S. GEL |  | LEAKS |  |  |
| 30/08/2017 | OFFLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 29/09/2017 | OFFLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 30/10/2017 | OFFLINE |  |  |  | NORMAL |  | FAIR |  | GOOD |  | NONE |  |  |
| 28/11/2017 | OFFLINE |  |  |  |  |  |  |  |  |  |  |  |  |
| 06/12/2017 | OFFLINE |  |  |  | LIQUID SCREEN TEST DATA |  |  |  |  |  |  |  |  |
|  |  | ASTM D974 |  |  |  |  |  |  |  |  | ASTM D4052 | ASTM D1524 | ASTM D1698 |
|  |  |  |  | ASTM D971 |  | IEC 156 |  | ASTM D1500 |  |  |  |  |  |
| DATE | SERVICES | ACID |  | IFT |  | DIEL |  | COLOUR |  |  | SP. GR. | VISUAL | ® SEDIMENT |
|  |  | (mgKOH/gm) |  | (mN/m) |  | (kV) |  |  |  |  |  |  |  |
| 04/07/2017 | ROUTINE | 0.020 AC |  | 31.2 QU |  | 62 AC |  | 1.0 AC |  |  | 0.8420 AC | CLEAR AC |  |
| 04/07/2017 | ROUTINE | 0.022 AC |  |  |  | 60 AC |  | 1.0 AC |  |  |  | CLEAR AC |  |
| 30/08/2017 | ROUTINE | 0.020 AC |  |  |  | 55 AC |  | 1.0 AC |  |  |  | CLEAR AC |  |
| 29/09/2017 | ROUTINE | 0.022 AC |  |  |  | 59 AC |  | 1.0 AC |  |  |  | CLEAR AC |  |
| 30/10/2017 | ROUTINE | 0.025 AC |  |  |  | 55 AC |  | 1.0 AC |  |  |  | CLEAR AC |  |
| 28/11/2017 | ROUTINE | 0.022 AC |  |  |  | 69 AC |  | 1.0 AC |  |  |  | CLEAR AC |  |
| 06/12/2017 | ROUTINE | 0.025 AC |  | 29.8 QU |  | 43 AC |  | 1.0 AC |  |  | 0.8471 AC | CLEAR AC |  |
|  |  | DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM |  |  |  |  |  |  |  |  |  |  |  |

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	10	18669	66036	3	24	665	ND	ND	ND	37	85407

06/12/2017	14	15414	63712	2	22	675	ND	ND	ND	38	79839

RECOMMENDATION:

RETEST 12 MONTHS:

TEST RESULT INDICATES NORMAL OPERATION.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	32	19	1.80	D

04/07/2017	31	15	1.42	C

30/08/2017	27	17	2.01	D

29/09/2017	29	15	1.58	C

30/10/2017	28	15	1.77	D

28/11/2017	29	16	1.68	C

06/12/2017	32	19	1.80	D

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK UNIT# - TRAFO 4 UNIT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0071084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 415 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

##### DATE	SERVICE

CENNIX LABORATORY SDN BHD 14 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | ND | ND | ND | ND |
| 06/12/2017 | ND | ND | ND | ND | ND | ND |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  ND	  ND	  ND

06/12/2017	  ND	  0.03	  ND

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	1.360 AC	04/07/2017	0.01 UN

06/12/2017	0.000 AC	 	0.370 AC	06/12/2017	0.03 UN

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	3A	MAGENTA

06/12/2017	NON-COR	1B	DARK ORANGE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK UNIT# - TRAFO 4 UNIT 3

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - ZHEJIAN |
| --- | --- |
| DATE MFG | - 2010 |
| MAIN TANK S/N | - 0071084208 |
| KVA | - |
| PRI | - 72000 V |
| SEC | - 415 V |
| KILOGRAMS | - 1350 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 731 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - NO

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 12. | ASH HANDLING | 10820108 | 15 |

A) Analysis

- Acidity of 0.017mgKOH/g and IFT of 37.5mN/m are ACCEPTABLE.

- Dielectric of 34kV is ACCEPTABLE.

- Specific gravity, Colour, and Visualization of oil is in the ACCEPTABLE range.

- The DGA result shows that Carbon Monoxide and Carbon Dioxide level are high. Other gases remain within normal limits and does not indicate any fault afflicting the transformer unit. Proceed with annual monitoring.

- Water Content in oil of 26ppm is ACCEPTABLE. Meanwhile Water Content in solid insulation of 1.85% M/dw is graded as B. For this transformer, it is recommended to maintain water content in oil at less than 30ppm.

- Furan analysis indicates the solid insulation is normal. None of furanic compound is detected.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.24% by weight is detected, thus ACCEPTABLE.

- Tested on copper strip resultant in multicolored with lavender blue and/or silver overlaid on claret red, thus Non-corrosive of 2C.

B) Recommendation

- Add passivator before the sulfur convert to be corrosive enough to attack copper. Passivator would coat the copper surface to retard or delay attack by corrosive sulfur.

- Do carry out *Liquid Screen Tests, Water Content, Furan Analysis, Metals-InOil, Liquid Power Factor and Inhibitor Content tests annually for Condition Monitoring purposes

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 23 of 25

### CENNIX LABORATORY (M) SDN BHD	     15

#### (Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE	STATUS	OIL TEMP °C	W. TEMP °C	OIL LEVEL	PAINT	S. GEL	LEAKS

04/07/2017	ONLINE	46

# 31/07/2017	ONLINE

30/08/2017	OFFLINE	30	NORMAL	FAIR	NONE

29/09/2017	OFFLINE	40	NORMAL	FAIR	NONE

30/10/2017	ONLINE	45	NORMAL	FAIR	NONE

# 27/11/2017	ONLINE	46

06/12/2017	ONLINE	52

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

04/07/2017	ROUTINE	    0.022 AC	38.1 AC	38 AC	   1.0 AC	     	0.8779 AC	CLEAR AC

31/07/2017	ROUTINE	    0.025 AC	 	56 AC	   1.0 AC	     	 	CLEAR AC

30/08/2017	ROUTINE	    0.022 AC	 	53 AC	   1.0 AC	     	 	CLEAR AC

29/09/2017	ROUTINE	    0.022 AC	 	57 AC	   1.0 AC	     	 	CLEAR AC

30/10/2017	ROUTINE	    0.022 AC	 	45 AC	   1.0 AC	     	 	CLEAR AC

27/11/2017	ROUTINE	    0.020 AC	 	36 AC	   1.0 AC	     	 	CLEAR AC

06/12/2017	ROUTINE	    0.017 AC	37.5 AC	34 AC	   1.0 AC	     	0.8832 AC	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

| 04/07/2017 | 35 | 10984 | 71058 | 20 | 441 | 5037 | 7 | 8 | ND | 511 | 87590 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 06/12/2017 | 49 | 12034 | 67124 | 20 | 558 | 5440 | 8 | 8 | ND | 643 | 85241 |

RECOMMENDATION:

CARBON MONOXIDE AND CARBON DIOXIDE LEVEL ARE HIGH. OTHER GASES LEVELS ARE ASSESSED AS ACCEPTABLE.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

| DATE | TEMP°C | PPM | %M/dw | GRADE |
| --- | --- | --- | --- | --- |
| 04/07/2017 | 34 | 28 | 2.30 | C |
| 31/07/2017 | 26 | 21 | 2.73 | D |
| 30/08/2017 | 28 | 16 | 1.89 | B |
| 29/09/2017 | 34 | 16 | 1.31 | B |
| 30/10/2017 | 33 | 20 | 1.64 | B |
| 27/11/2017 | 36 | 29 | 2.06 | C |
| 06/12/2017 | 36 | 26 | 1.85 | B |

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK UNIT# - ASH HANDLING

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

MFG	 - WOLONG

DATE MFG	 - 2011

MAIN TANK S/N	 - 10820108

KVA	 - 1600

PRI	 - 6300 V

SEC	 - 400 V

KILOGRAMS	 - 4505

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 - 5.56%

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 1023

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

##### DATE	SERVICE

CENNIX LABORATORY SDN BHD 15 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | ND | ND | ND | ND |
| 06/12/2017 | ND | ND | ND | ND | ND | ND |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  ND	  0.01	  0.01

06/12/2017	  ND	  ND	  0.01

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	0.730 AC	04/07/2017	0.23 AC

06/12/2017	0.000 AC	 	0.240 AC	06/12/2017	0.24 AC

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	1B	DARK ORANGE

06/12/2017	NON-COR	2C	LAVENDER BLUE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK UNIT# - ASH HANDLING

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - WOLONG |
| --- | --- |
| DATE MFG | - 2011 |
| MAIN TANK S/N | - 10820108 |
| KVA | - 1600 |
| PRI | - 6300 V |
| SEC | - 400 V |
| KILOGRAMS | - 4505 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - 5.56% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 1023 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - YES CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - YES HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

| No. | Unit No. | Serial Number | TC |
| --- | --- | --- | --- |
| 13. | ASH HANDLING | 10820107 | 16 |

A) Analysis

- Acidity of 0.020mgKOH/g and IFT of 36.6mN/m are ACCEPTABLE.

- Dielectric of 24kV is UNACCEPTABLE. This is reflected from the high moisture content detected in the transformer oil.

- Specific gravity, Colour, and Visualization of oil is in the ACCEPTABLE range.

- Dissolved Gas Analysis shows significant amount of Carbon Dioxide while other gases remain within normal limits and does not indicate any fault afflicting the transformer unit. Proceed with annual monitoring.

- Water Content in oil of 32ppm is UNACCEPTABLE. Meanwhile Water Content in solid insulation of 2.62% M/dw is graded as D. For this transformer, it is recommended to maintain water content in oil at less than 30ppm. This indicates the presence of high water content in the oil.

The presence of high water content could cause dielectric failure.

- Furanic compound 2FAL of 3ppb was detected which indicates normal

aging of the solid insulation.

- Metals-In-Oil detected are below 2ppm, thus ACCEPTABLE.

- Liquid Power Factors at both 25ºC and 100ºC are ACCEPTABLE.

- Oil Inhibitor of 0.24% by weight is detected, thus ACCEPTABLE.

- Corrosive sulfur test on copper strip resultant in light orange, thus Noncorrosive of 1A.

B) Recommendation

- Highly recommended to perform OIL PURIFICATION. Result indicates that the moisture content in the transformer oil is not conducive for normal operation of a transformer. Oil purification will remove excessive moisture detected in the transformer oil and thus improving dielectric breakdown voltage of the mineral oil. Furthermore, passivator will be added to preserve both the transformer oil and copper surfaces to enhance the service ability of the transformer

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 24 of 25

### CENNIX LABORATORY (M) SDN BHD	     16

#### (Formerly known as Myers-Musteq Sdn Bhd)

VISUAL INSPECTION

DATE	STATUS	OIL TEMP °C	W. TEMP °C	OIL LEVEL	PAINT	S. GEL	LEAKS

04/07/2017	ONLINE	40

31/07/2017	ONLINE

30/08/2017	ONLINE	47	NORMAL	FAIR	NONE

29/09/2017	ONLINE	60	NORMAL	FAIR	NONE

30/10/2017	OFFLINE	32	NORMAL	FAIR	NONE

27/11/2017	OFFLINE	40

06/12/2017	ONLINE	48

LIQUID SCREEN TEST DATA

ASTM D974	ASTM D971	IEC 156	ASTM D1500	ASTM D4052	ASTM D1524	ASTM D1698

®

DATE	SERVICES	ACID	IFT	DIEL	COLOUR	 SP. GR.	 VISUAL	SEDIMENT

(mgKOH/gm)	(mN/m)	(kV)

04/07/2017	ROUTINE	    0.022 AC	37.3 AC	36 AC	   1.0 AC	     	0.8788 AC	CLEAR AC

31/07/2017	ROUTINE	    0.022 AC	 	40 AC	   1.0 AC	     	 	CLEAR AC

30/08/2017	ROUTINE	    0.022 AC	 	31 AC	   1.5 AC	     	 	CLEAR AC

29/09/2017	ROUTINE	    0.022 AC	 	28 QU	   1.5 AC	     	 	CLEAR AC

30/10/2017	ROUTINE	    0.020 AC	 	46 AC	   1.5 AC	     	 	CLEAR AC

27/11/2017	ROUTINE	    0.022 AC	 	47 AC	   1.5 AC	     	 	CLEAR AC

06/12/2017	ROUTINE	    0.020 AC	36.6 AC	24 UN	   1.5 AC	     	0.8840 AC	CLEAR AC

DISSOLVED GAS ANALYSIS (ASTM D3612), EXPRESSED IN PPM

CARBON	CARBON	TOTAL	TOTAL

DATE	HYDROGEN OXYGEN	NITROGEN	METHANE MONOXIDE DIOXIDE ETHANE ETHYLENE ACETYLENE COMBUSTIBLE	GAS

04/07/2017	18	21157	64224	4	129	1676	ND	1	ND	152	87209

06/12/2017	20	15791	63530	5	275	2783	ND	4	ND	304	82408

RECOMMENDATION:

CARBON DIOXIDE GAS LEVEL IS HIGH.OTHER GASES ARE ASSESSED AS ACCEPTABLE.

WATER CONTENT (ASTM D1533), EXPRESSED IN PPM

DATE	TEMP°C	PPM	%M/dw	GRADE

04/07/2017	29	21	2.20	C

31/07/2017	31	32	3.04	D

30/08/2017	34	29	2.38	C 29/09/2017	40	31	1.71	B

30/10/2017	29	21	2.20	C

27/11/2017	29	20	2.10	C

06/12/2017	34	32	2.62	D

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK UNIT# - ASH HANDLING

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

MFG	 - WOLONG

DATE MFG	 - 2011

MAIN TANK S/N	 - 1082017

KVA	 - 1600

PRI	 - 6300 V

SEC	 - 400 V

KILOGRAMS	 - 4505

EQUIP TYPE	 - TRANSFORMER

TRANS CLASS	 - ONAN

IMPEDENCE	 - 5.6%

PHASE/CYCLE	 - 3/50 Hz

LIQUID TYPE	 - OIL

LITRES LIQUID	 - 1023

LTC MFG	 -

LTC S/N	 -

LTC FAB NO	 -

LTC MODEL	 -

LTC LITRES LIQUID	 -

LTC ENERGIZED	 -

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - NO CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - NO HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

##### DATE	SERVICE

CENNIX LABORATORY SDN BHD 16 (Formerly known as Myers-Musteq Sdn Bhd)

FURAN ANALYSIS (ASTM D5837), EXPRESSED IN PPB

| DATE | 5H2F | 2FOL | 2FAL | 2ACF | 5M2F | TOTAL |
| --- | --- | --- | --- | --- | --- | --- |
| 04/07/2017 | ND | ND | ND | ND | ND | ND |
| 06/12/2017 | ND | ND | 3 | ND | ND | 3 |

RECOMMENDATION:

RETEST 12  MONTHS:

TEST RESULT OBTAINED IN THIS TEST IS IN LINE WITH A HEALTHY PAPER INSULATION OF TRANSFORMER.

METALS-IN-OIL (ASTM D3635), EXPRESSED IN PPM

®	®

DATE	ALUMINIUM	 IRON	COPPER

04/07/2017	  ND	  0.01	  ND

06/12/2017	  ND	  0.01	  0.01

LIQUID POWER FACTOR (ASTM D924)	INHIBITOR CONTENT, DBPC (ASTM D2668)

DATE	25°C	100°C	   DATE	%BY WEIGHT

04/07/2017	0.000 AC	 	1.350 AC	04/07/2017	0.22 AC

06/12/2017	0.000 AC	 	0.270 AC	06/12/2017	0.24 AC

®	®

CORROSIVE SULFUR (ASTM 1275B) 	PASSIVATOR COUNT, EXPRESSED IN PPM

DATE	STATUS	CLASS	APPEARANCE	DATE	PPM

04/07/2017	NON-COR	3A	MAGENTA

06/12/2017	NON-COR	1A	LIGHT ORANGE

DATE PRINTED 23/12/2017

ID# - 601669

#### CUST - PT IP UJP PLTU JERANJANG

SUB NAME - CITY - MATARAM LOMBOK UNIT# - ASH HANDLING

LOCATION - OUTDOOR OTHER -

##### NAMEPLATE DATA

| MFG | - WOLONG |
| --- | --- |
| DATE MFG | - 2011 |
| MAIN TANK S/N | - 1082017 |
| KVA | - 1600 |
| PRI | - 6300 V |
| SEC | - 400 V |
| KILOGRAMS | - 4505 |
| EQUIP TYPE | - TRANSFORMER |
| TRANS CLASS | - ONAN |
| IMPEDENCE | - 5.6% |
| PHASE/CYCLE | - 3/50 Hz |
| LIQUID TYPE | - OIL |
| LITRES LIQUID | - 1023 |
| LTC MFG | - |
| LTC S/N | - |
| LTC FAB NO | - |
| LTC MODEL | - |
| LTC LITRES LIQUID | - |
| LTC ENERGIZED | - |

ADDITIONAL EQUIPMENT

RADIATORS	 - YES FANS	 - NO H2O COOLED	 - NO OIL PUMPS	 - NO TOP FPV	 BOTTOM FPV BUCHOLZ - NO CONSERVATOR	 - YES LTC COMPARTMENT - NO BUSHING LOC	 - TOP FREE BREATHER	 - NO HOSE LENGTH	 POWER AVAILABLE	 - YES

FIELD SERVICE

DATE	SERVICE

#### Ref No : TXM/MKT-1200/SA/CI17049

3.0 	Summary of Our Comments & Recommendations:

| No. | Sub Name | Unit No. | TC | Recommendation |
| --- | --- | --- | --- | --- |
| 1. | MAIN TRAFO UNIT 1 | 1006901 | 4 | - Retest 6 months: DGA - Add passivator - Other parameters: Periodic condition monitoring |
| 2. | TRAFO 1 ESP UNIT 1 | 10937 | 5 |  Perform OIL REGENERATION |
| 3. | TRAFO 2 ESP UNIT 1 | 10035 | 6 |  Perform OIL REGENERATION |
| 4. | TRAFO 3 ESP UNIT 1 | 10031 | 7 | - Retest 6 months: Acidity and IFT - Add inhibitor 2,6-DBPC and passivator - Other parameters: Periodic condition monitoring |
| 5. | TRAFO 4 ESP UNIT 1 | 10034 | 8 |  Perform OIL REGENERATION |
| 6. | MAIN TRAFO UNIT 3 | 1122170 | 9 | - Add passivator - Periodic condition monitoring |
| 7. | UAT 3 | 1035082 | 10 | - Add passivator - Periodic condition monitoring |
| 8. | TRAFO 1 ESP UNIT 3 | 007308428 | 11 |  Perform OIL PURIFICATION |
| 9. | TRAFO 2 ESP UNIT 3 | 0070084208 | 12 |  Perform OIL REGENERATION |
| 10. | TRAFO 3 ESP UNIT 3 | 0072084208 | 13 |  Perform OIL PURIFICATION |
| 11. | TRAFO 4 UNIT 3 | 0071084208 | 14 | - Retest 6 months: Acidity and IFT - Add inhibitor 2,6-DBPC and passivator - Other parameters: Periodic condition monitoring |
| 12. | ASH HANDLING | 10820108 | 15 | - Add passivator - Periodic condition monitoring |
| 13. | ASH HANDLING | 10820107 | 16 |  Perform OIL PURIFICATION |

Page Disclaimer :

All information provided is deemed reliable but is not guaranteed. The interpretation, comments and recommendations are derived based on International Standards and are the personal opinion of the Analyst of TxM Services Sdn. Bhd. The customer is advised to independently verify the information

herein

Page 25 of 25

| no | Test Cer. | Date Test | nama unit |  | Serial number | thn opr | Jumlah minyak, liter | Buatan | hasil tes |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | acid | ift | diel. | color | spec. Graf. | visual | sedi. | moisture |  | dga ASTM |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ppm | grade | H2 | O2 | N2 | CH4 | CO |
| Standard yang dipakai |  |  |  |  |  |  |  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | ASTM D1533 |  | hydrogen | oksigen | nitrogen | methane | carbon monoksida |
|  | BATASAN OPERASI |  |  |  |  |  |  |  | < 0,06 | > 32 | > 30 | < 3,5 | > 0,84 | C |  | < 20 |  | < 100 |  |  | < 120 | < 350 |
| 1 | 1 | 27/02/17 | Main trafo | 1 | 1006901 | 2011 | 30.857 | Wolong | 0,014 | 39,9 | 99 | 0,5 | 0,8693 | C |  | 9 | A | 135 | 15.834 | 57.625 | 27 | 807 |
|  | 4 | 04/07/17 |  |  |  |  |  |  | 0,017 | 41,5 | 58 | 0,5 | 0,8691 | C |  | 10 | A | 147 | 9.471 | 4.328 | 32 | 655 |
|  | 4 | 30/07/2017 |  |  |  |  |  |  | 0,017 |  | 70 | 0,5 |  | C |  | 8 | B |  |  |  |  |  |
|  | 4 | 30/08/2017 |  |  |  |  |  |  | 0,017 |  | 92 | 0,5 |  | C |  | 6 | A |  |  |  |  |  |
|  | 4 | 29/09/2017 |  |  |  |  |  |  | 0,014 |  | 82 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |
|  | 4 | 30/10/2017 |  |  |  |  |  |  | 0,014 |  | 82 | 0,5 |  | C |  | 6 | A |  |  |  |  |  |
|  | 4 | 27/11/2017 |  |  |  |  |  |  | 0,014 |  | 53 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |
|  | 4 | 07/12/2017 |  |  |  |  |  |  | 0,011 | 40,1 | 87 | 0,5 | 0,8745 | C |  | 7 | A | 183 | 12.895 | 43.794 | 39 | 715 |
| 2 | 5 | 04/07/17 | Trafo 1 ESP | 1 | 10937 | 2010 | 1.143 | Fujia | 0,056 | 25,3 | 50 | 1,5 | 0,8529 | C |  | 18 | D | 35 | 20.494 | 67.487 | 4 | 69 |
|  | 5 | 30/07/2017 |  |  |  |  |  |  | 0,059 |  | 57 | 1,5 |  | C |  | 20 | D |  |  |  |  |  |
|  | 5 | 30/08/2017 |  |  |  |  |  |  | 0,056 |  | 65 | 1,5 |  | C |  | 18 | D |  |  |  |  |  |
|  | 5 | 29/09/2017 |  |  |  |  |  |  | 0,059 |  | 58 | 1,5 |  | C |  | 19 | D |  |  |  |  |  |
|  | 5 | 30/10/2017 |  |  |  |  |  |  | 0,059 |  | 23 | 1,5 |  | C |  | 32 | C |  |  |  |  |  |
|  | 5 | 27/11/2017 |  |  |  |  |  |  | 0,062 |  | 25 | 1,5 |  | C |  | 33 | C |  |  |  |  |  |
|  | 5 | 07/12/2017 |  |  |  |  |  |  |  | 25,0 | 49 | 1,5 | 0,8593 | C |  | 18 | D | 39 | 19.933 | 67.198 | 4 | 83 |
| 3 | 6 | 04/07/17 | Trafo 2 ESP | 1 | 10035 | 2010 | 1.143 | Fujia | 0,042 | 26,6 | 41 | 1,5 | 0,8540 | C |  | 21 | D | 27 | 18.639 | 66.781 | 3 | 64 |
|  | 6 | 30/07/2017 |  |  |  |  |  |  | 0,045 |  | 25 | 1,5 |  | C |  | 27 | E |  |  |  |  |  |
|  | 6 | 30/08/2017 |  |  |  |  |  |  | 0,042 |  | 42 | 1,5 |  | C |  | 14 | C |  |  |  |  |  |
|  | 6 | 29/09/2017 |  |  |  |  |  |  | 0,048 |  | 59 | 1,5 |  | C |  | 19 | D |  |  |  |  |  |
|  | 6 | 30/10/2017 |  |  |  |  |  |  | 0,051 |  | 62 | 1,5 |  | C |  | 17 | B |  |  |  |  |  |
|  | 6 | 27/11/2017 |  |  |  |  |  |  | 0,051 |  | 50 | 1,5 |  | C |  | 18 | B |  |  |  |  |  |
|  | 6 | 07/12/2017 |  |  |  |  |  |  | 0,063 | 27,3 | 51 | 1,5 | 0,8589 | C |  | 17 | D | 20 | 19.360 | 61.590 | 3 | 45 |
| 4 | 7 | 04/07/17 | Trafo 3 ESP | 1 | 10031 | 2010 | 1.143 | Fujia | 0,048 | 28,4 | 44 | 1,0 | 0,8537 | C |  | 32 | E | 32 | 15.273 | 65.111 | 5 | 95 |
|  | 7 | 30/07/2017 |  |  |  |  |  |  | 0,042 |  | 77 | 1,5 |  |  |  | 10 | D |  |  |  |  |  |
|  | 7 | 30/08/2017 |  |  |  |  |  |  | 0,042 |  | 61 | 1,5 |  | C |  | 13 | C |  |  |  |  |  |
|  | 7 | 29/09/2017 |  |  |  |  |  |  | 0,045 |  | 72 | 1,5 |  | C |  | 14 | B |  |  |  |  |  |
|  | 7 | 30/10/2017 |  |  |  |  |  |  | 0,048 |  | 72 | 1,5 |  | C |  | 16 | B |  |  |  |  |  |
|  | 7 | 27/11/2017 |  |  |  |  |  |  | 0,051 |  | 62 | 1,5 |  | C |  | 17 | C |  |  |  |  |  |
|  | 7 | 07/12/2017 |  |  |  |  |  |  | 0,063 | 29,3 | 57 | 1,5 | 0,8624 | C |  | 16 | C | 7 | 14.730 | 65.738 | 3 | 42 |
| 5 | 8 | 04/07/17 | Trafo 4 ESP | 1 | 10034 | 2010 | 1.143 | Fujia | 0,028 | 26,3 | 24 | 1,5 | 0,8596 | C |  | 29 | E | 13 | 12.265 | 66.770 | 5 | 172 |
|  | 8 | 30/07/2017 |  |  |  |  |  |  | 0,022 |  | 88 | 1,5 |  | C |  | 15 | D |  |  |  |  |  |
|  | 8 | 30/08/2017 |  |  |  |  |  |  | 0,028 |  | 44 | 1,5 |  | C |  | 13 | C |  |  |  |  |  |
|  | 8 | 29/09/2017 |  |  |  |  |  |  | 0,031 |  | 53 | 1,0 |  | C |  | 15 | B |  |  |  |  |  |
|  | 8 | 30/10/2017 |  |  |  |  |  |  | 0,028 |  | 48 | 1,0 |  | C |  | 18 | B |  |  |  |  |  |
|  | 8 | 27/11/2017 |  |  |  |  |  |  | 0,034 |  | 41 | 1,5 |  | C |  | 30 | D |  |  |  |  |  |
|  | 8 | 07/12/2017 |  |  |  |  |  |  | 0,031 | 27,2 | 41 | 1,5 | 0,8645 | C |  | 18 | D | 9 | 13.331 | 63.527 | 3 | 70 |
| 6 | 2 | 27/02/17 | Main trafo | 3 | 1122170 | 2010 | 26.706 | Shandong | 0,017 | 39,7 | 87 | 0,5 | 0,8781 | C |  | 9 | A | 4 | 13.330 | 43.140 | 9 | 808 |
|  | 9 | 04/07/17 |  |  |  |  |  |  | 0,017 | 42,3 | 78 | 0,5 | 0,8780 | C |  | 15 | B | 24 | 10.131 | 44.084 | 11 | 641 |
|  | 9 | 30/07/2017 |  |  |  |  |  |  | 0,014 |  | 77 | 0,5 |  | C |  | 17 | B |  |  |  |  |  |
|  | 9 | 30/08/2017 |  |  |  |  |  |  | 0,017 |  | 86 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |
|  | 9 | 29/09/2017 |  |  |  |  |  |  | 0,014 |  | 86 | 0,5 |  | C |  | 10 | A |  |  |  |  |  |
|  | 9 | 30/10/2017 |  |  |  |  |  |  | 0,014 |  | 88 | 0,5 |  | C |  | 9 | A |  |  |  |  |  |

| no | Test Cer. | Date Test | nama unit |  | Serial number | thn opr | Jumlah minyak, liter | Buatan | hasil tes |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | acid | ift | diel. | color | spec. Graf. | visual | sedi. | moisture |  | dga ASTM |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ppm | grade | H2 | O2 | N2 | CH4 | CO |
| Standard yang dipakai |  |  |  |  |  |  |  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | ASTM D1533 |  | hydrogen | oksigen | nitrogen | methane | carbon monoksida |
|  | BATASAN OPERASI |  |  |  |  |  |  |  | < 0,06 | > 32 | > 30 | < 3,5 | > 0,84 | C |  | < 20 |  | < 100 |  |  | < 120 | < 350 |
|  | 9 | 27/11/2017 |  |  |  |  |  |  | 0,014 |  | 87 | 0,5 |  | C |  | 8 | A |  |  |  |  |  |
|  | 9 | 07/12/2017 |  |  |  |  |  |  | 0,014 | 41,5 | 84 | 0,5 | 0,8932 | C |  |  | A | 39 | 14.023 | 43.226 | 11 | 668 |
| 7 | 3 | 27/02/17 | Trafo UAT | 3 | 1035082 | 2010 | 4.749 | Shandong | 0,017 | 37,6 | 94 | 0,5 | 0,8768 | C |  | 9 | A | 20 | 12.535 | 56.879 | 20 | 985 |
|  | 10 | 04/07/17 |  |  |  |  |  |  | 0,022 | 38,1 | 60 | 0,5 | 0,8767 | C |  | 11 | A | 20 | 16.028 | 68.308 | 20 | 971 |
|  | 10 | 30/07/2017 |  |  |  |  |  |  | 0,025 |  | 88 | 0,5 |  | C |  | 14 | B |  |  |  |  |  |
|  | 10 | 30/08/2017 |  |  |  |  |  |  | 0,022 |  | 89 | 0,5 |  | C |  | 11 | A |  |  |  |  |  |
|  | 10 | 29/09/2017 |  |  |  |  |  |  | 0,020 |  | 80 | 0,5 |  | C |  | 12 | A |  |  |  |  |  |
|  | 10 | 30/10/2017 |  |  |  |  |  |  | 0,022 |  | 86 | 0,5 |  | C |  | 11 | A |  |  |  |  |  |
|  | 10 | 27/11/2017 |  |  |  |  |  |  | 0,022 |  | 86 | 0,5 |  | C |  | 12 | A |  |  |  |  |  |
|  | 10 | 07/12/2017 |  |  |  |  |  |  | 0,020 | 37,6 | 86 | 0,5 | 0,8200 | C |  | 12 | A | 36 | 18.752 | 66.758 | 1 | 1.116 |
| 8 | 11 | 04/07/17 | Trafo 1 ESP | 3 | 007308428 | 2010 | 731 | Zhejian | 0,022 | 23,2 | 32 | 1,5 | 0,8432 | C |  | 26 | D | 14 | 12.943 | 68.807 | 3 | 62 |
|  | 11 | 30/07/2017 |  |  |  |  |  |  | 0,028 |  | 47 | 1,5 |  | C |  | 21 | D |  |  |  |  |  |
|  | 11 | 30/08/2017 |  |  |  |  |  |  | 0,028 |  | 36 | 1,5 |  | C |  | 22 | D |  |  |  |  |  |
|  | 11 | 29/09/2017 |  |  |  |  |  |  | 0,025 |  | 45 | 1,5 |  | C |  | 20 | C |  |  |  |  |  |
|  | 11 | 30/10/2017 |  |  |  |  |  |  | 0,025 |  | 40 | 1,5 |  | C |  | 19 | D |  |  |  |  |  |
|  | 11 | 27/11/2017 |  |  |  |  |  |  | 0,025 |  | 31 | 1,5 |  | C |  | 34 | C |  |  |  |  |  |
|  | 11 | 07/12/2017 |  |  |  |  |  |  | 0,022 | 34,6 | 31 | 1,5 | 0,8190 | C |  | 31 | C | 14 | 12.739 | 65.097 | 3 | 66 |
| 9 | 12 | 04/07/17 | Trafo 2 ESP | 3 | 007008428 | 2010 | 731 | Zhejian | 0,118 | 16,2 | 24 | 3,0 | 0,8435 | C |  | 39 | D | 38 | 16.781 | 70.523 | 5 | 129 |
|  | 12 | 30/07/2017 |  |  |  |  |  |  | 0,112 |  | 28 | 3,0 |  | C |  | 38 | E |  |  |  |  |  |
|  | 12 | 30/08/2017 |  |  |  |  |  |  | 0,109 |  | 34 | 2,5 |  | C |  | 17 | D |  |  |  |  |  |
|  | 12 | 29/09/2017 |  |  |  |  |  |  | 0,115 |  | 21 | 2,5 |  | C |  | 37 | D |  |  |  |  |  |
|  | 12 | 30/10/2017 |  |  |  |  |  |  | 0,118 |  | 33 | 2,5 |  | C |  | 20 | D |  |  |  |  |  |
|  | 12 | 27/11/2017 |  |  |  |  |  |  | 0,017 |  | 25 | 0,5 |  | C |  | 28 | B |  |  |  |  |  |
|  | 12 | 07/12/2017 |  |  |  |  |  |  | 0,022 | 29,7 | 29 | 0,1 | 0,8106 | C |  | 44 | D | 42 | 19.523 | 66.059 | 3 | 102 |
| 10 | 13 | 04/07/17 | Trafo 3 ESP | 3 | 007208428 | 2010 | 731 | Zhejian | 0,025 | 27,8 | 40 | 1,5 | 0,8415 | C |  | 27 | D | 21 | 16.364 | 70.694 | 3 | 38 |
|  | 13 | 30/07/2017 |  |  |  |  |  |  | 0,025 |  | 66 | 1,5 |  | C |  | 18 | D |  |  |  |  |  |
|  | 13 | 30/08/2017 |  |  |  |  |  |  | 0,025 |  | 50 | 1,5 |  | C |  | 21 | C |  |  |  |  |  |
|  | 13 | 29/09/2017 |  |  |  |  |  |  | 0,028 |  | 59 | 1,5 |  | C |  | 22 | C |  |  |  |  |  |
|  | 13 | 30/10/2017 |  |  |  |  |  |  | 0,028 |  | 55 | 1,5 |  | C |  | 28 | D |  |  |  |  |  |
|  | 13 | 27/11/2017 |  |  |  |  |  |  | 0,014 |  | 39 | 0,5 |  | C |  | 24 | B |  |  |  |  |  |
|  | 13 | 07/12/2017 |  |  |  |  |  |  | 0,014 | 39,8 | 45 | 0,5 | 0,8099 | C |  | 29 | B | 15 | 14.515 | 65.277 | 2 | 40 |
| 11 | 14 | 04/07/17 | Trafo 4 ESP | 3 | 007108428 | 2010 | 731 | Zhejian | 0,020 | 31,2 | 62 | 1,0 | 0,8420 | C |  | 19 | D | 10 | 18.669 | 66.036 | 3 | 24 |
|  | 14 | 30/07/2017 |  |  |  |  |  |  | 0,022 |  | 60 | 1,0 |  | C |  | 15 | C |  |  |  |  |  |
|  | 14 | 30/08/2017 |  |  |  |  |  |  | 0,020 |  | 55 | 1,0 |  | C |  | 17 | D |  |  |  |  |  |
|  | 14 | 29/09/2017 |  |  |  |  |  |  | 0,022 |  | 59 | 1,0 |  | C |  | 15 | C |  |  |  |  |  |
|  | 14 | 30/10/2017 |  |  |  |  |  |  | 0,025 |  | 55 | 1,0 |  | C |  | 15 | D |  |  |  |  |  |
|  | 14 | 27/11/2017 |  |  |  |  |  |  | 0,022 |  | 69 | 1,0 |  | C |  | 16 | C |  |  |  |  |  |
|  | 14 | 07/12/2017 |  |  |  |  |  |  | 0,025 | 29,8 | 43 | 1,0 | 0,8471 | C |  | 19 | D | 14 | 15.414 | 63.712 | 2 | 22 |
| 12 | 15 | 04/07/17 | Ash Handling |  | 10820108 | 2011 | 1.023 | Wolong | 0,022 | 38,1 | 38 | 1,0 | 0,8779 | C |  | 28 | C | 35 | 10.984 | 71.058 | 20 | 441 |
|  | 15 | 30/07/2017 |  |  |  |  |  |  | 0,025 |  | 56 | 1,0 |  | C |  | 21 | D |  |  |  |  |  |
|  | 15 | 30/08/2017 |  |  |  |  |  |  | 0,022 |  | 53 | 1,0 |  | C |  | 16 | B |  |  |  |  |  |
|  | 15 | 29/09/2017 |  |  |  |  |  |  | 0,022 |  | 57 | 1,0 |  | C |  | 16 | B |  |  |  |  |  |
|  | 15 | 30/10/2017 |  |  |  |  |  |  | 0,022 |  | 45 | 1,0 |  | C |  | 20 | B |  |  |  |  |  |
|  | 15 | 27/11/2017 |  |  |  |  |  |  | 0,020 |  | 36 | 1,0 |  | C |  | 29 | C |  |  |  |  |  |
|  | 15 | 07/12/2017 |  |  |  |  |  |  | 0,017 | 37,5 | 34 | 1,0 | 0,8932 | C |  | 26 | B | 49 | 12.034 | 67.124 | 20 | 558 |

| no | Test Cer. | Date Test | nama unit |  | Serial number | thn opr | Jumlah minyak, liter | Buatan |  |  |  |  |  |  |  |  |  |  |  |  |  | hasil tes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | acid | ift | diel. | color | spec. Graf. | visual | sedi. | moisture |  |  |  |  |  | dga ASTM |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | ppm | grade | H2 | O2 | N2 | CH4 | CO |
|  |  | Standard yang dipakai |  |  |  |  |  |  | ASTM D974 | ASTM D971 | IEC 156 | ASTM D1500 | ASTM D4052 | ASTM D1524 | ASTM D1698 | ASTM D1533 |  | hydrogen | oksigen | nitrogen | methane | carbon monoksida |
|  |  |  |  |  |  |  | BATASAN OPERASI |  | < 0,06 | > 32 | > 30 | < 3,5 | > 0,84 | C |  | < 20 |  | < 100 |  |  | < 120 | < 350 |
| 13 | 16 | 04/07/17 | Ash Handling |  | 10820107 | 2011 | 1.023 | Wolong | 0,022 | 37,3 | 36 | 1,0 | 0,8788 | C |  | 21 | C | 18 | 21.157 | 64.224 | 4 | 129 |
|  | 16 | 30/07/2017 |  |  |  |  |  |  | 0,022 |  | 40 | 1,0 |  | C |  | 32 | D |  |  |  |  |  |
|  | 16 | 30/08/2017 |  |  |  |  |  |  | 0,022 |  | 31 | 1,0 |  | C |  | 29 | C |  |  |  |  |  |
|  | 16 | 29/09/2017 |  |  |  |  |  |  | 0,022 |  | 28 | 1,5 |  | C |  | 31 | B |  |  |  |  |  |
|  | 16 | 30/10/2017 |  |  |  |  |  |  | 0,020 |  | 46 | 1,5 |  | C |  | 21 | C |  |  |  |  |  |
|  | 16 | 27/11/2017 |  |  |  |  |  |  | 0,022 |  | 47 | 1,5 |  | C |  | 20 | C |  |  |  |  |  |
|  | 16 | 07/12/2017 |  |  |  |  |  |  | 0,020 | 36,6 | 24 | 1,5 | 0,8940 | C |  | 32 | D | 20 | 15.791 | 63.530 | 5 | 275 |

| no | Test Cer. | Date Test | st laboratorium cennix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | nama unit D3612 |  |  |  |  |  |  | lpf (C) |  | dbpc | furan |  | metal in oil |  |  | corr. sul | keterangan |
|  |  |  |  |  | CO2 | C2H6 | C2H4 | C2H2 | TOT | 25O | 100O |  |  | Al |  | Fe | Cu |  |  |
| Standa |  |  |  |  | carbon r dioksida | ethane | ethylene | acethylene |  | ASTM D924 |  | ASTM D2668 | ASTM D5837 |  | ASTM D3635 |  |  | ASTM D1275B |  |
|  |  |  |  |  | < 2.500 | < 65 | <50 | < 2 | < 687 | < 0.1 | < 2.9 | > .2 | < 100 | 0,00 |  | 0,00 | 0,00 |  | Non corrosive |
| 1 | 1 | 27/02/17 | Main trafo | 1 | 3.099 | 3 | 4 | 0 | 976 843 | 0,000 | 0,070 | 0,32 | 0 | 0,00 |  | 0,00 | 0,01 | 1B | Non Corrosive |
|  | 4 | 04/07/17 |  |  | 2.728 | 4 | 5 | 0 |  | 0,000 | 0,140 | 0,24 | 0 | 0,02 |  | 0,01 | 0,01 | 3 A | Suspec Corrosive |
|  | 4 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 4 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 4 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 4 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 4 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 4 | 07/12/2017 |  |  | 3.166 | 5 | 5 | 0 | 947 | 0,000 | 0,040 | 0,27 | 0 | 0,00 |  | 0,01 | 0,04 | 2C | Non corrosive |
| 2 | 5 | 04/07/17 | Trafo 1 ESP | 1 | 1.143 | 0 | 1 | 0 | 109 | 0,000 | 1,870 | 0,00 | 95 | 0,00 |  | 0,01 | 0,01 | 1 B | Non Corrosive |
|  | 5 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5 | 07/12/2017 |  |  | 1.261 | 0 | 1 | 0 | 127 | 0,000 | 0,570 | 0,00 | 75 | 0,00 |  | 0,00 | 0,00 | 1A | Non corrosive |
| 3 | 6 | 04/07/17 | Trafo 2 ESP | 1 | 1.106 | 0 | 1 | 0 | 95 | 0,000 | 1,900 | 0,02 | 62 | 0,00 |  | 0,01 | 0,00 | 1 A | Non Corrosive |
|  | 6 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6 | 07/12/2017 |  |  | 729 | 0 | 1 | 0 | 69 | 0,000 | 0,980 | 0,02 | 67 | 0,00 |  | 0,00 | 0,02 | 1B | Non corrosive |
| 4 | 7 | 04/07/17 | Trafo 3 ESP | 1 | 1.002 | 0 | 2 | 0 | 134 | 0,000 | 1,700 | 0,01 | 32 | 0,01 |  | 0,01 | 0,01 | 1 A | Non corrosive |
|  | 7 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 7 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 7 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 7 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 7 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 7 | 07/12/2017 |  |  | 617 | 0 | 0 | 0 | 52 | 0,000 | 0,630 | 0,01 | 14 | 0,00 |  | 0,00 | 0,00 | 2C | Non corrosive |
| 5 | 8 | 04/07/17 | Trafo 4 ESP | 1 | 1.206 | 0 | 8 | 0 | 198 | 0,180 | 6,680 | 0,08 | 18 | 0,05 |  | 0,02 | 0,01 | 2 C | Non Corrosive |
|  | 8 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8 | 07/12/2017 |  |  | 720 | 0 | 1 | 0 | 83 | 0,010 | 2,180 | 0,06 | 0 | 0,00 |  | 0,00 | 0,02 | 2C | Non corrosive |
| 6 | 2 | 27/02/17 | Main trafo | 3 | 2.878 | 0 | 1 | 0 | 822 | 0,000 | 0,090 | 0,30 | 0 | 0,00 |  | 0,03 | 0,02 | 1A | Non corrosive |
|  | 9 | 04/07/17 |  |  | 2.250 | 1 | 1 | 0 | 678 | 0,000 | 0,130 | 0,22 | 0 | 0,01 |  | 0,01 | 0,02 | 3 A | Suspec Corrosive |
|  | 9 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| no | Test Cer. | Date Test | st laboratorium cennix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | nama unit D3612 |  |  |  |  |  |  | lpf (C) |  | dbpc | furan |  | metal in oil |  |  | corr. sul | keterangan |
|  |  |  |  |  | CO2 | C2H6 | C2H4 | C2H2 | TOT | 25O | 100O |  |  | Al |  | Fe | Cu |  |  |
| Standa |  |  |  |  | carbon r dioksida | ethane | ethylene | acethylene |  | ASTM D924 |  | ASTM D2668 | ASTM D5837 |  | ASTM D3635 |  |  | ASTM D1275B |  |
|  |  |  |  |  | < 2.500 | < 65 | <50 | < 2 | < 687 | < 0.1 | < 2.9 | > .2 | < 100 | 0,00 |  | 0,00 | 0,00 |  | Non corrosive |
|  | 9 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9 | 07/12/2017 |  |  | 2.456 | 0 | 1 | 0 | 719 | 0,000 | 0,070 | 0,22 | 0 | 0,01 |  | 0,00 | 0,03 | 2C | Non corrosive |
| 7 | 3 | 27/02/17 | Trafo UAT | 3 | 3.877 | 6 | 7 | 0 | 1.038 | 0,000 | 0,100 | 0,30 | 0 | 0,00 |  | 0,01 | 0,04 | 1A | Non Corrosive |
|  | 10 | 04/07/17 |  |  | 3.536 | 5 | 7 | 0 | 1.023 | 0,000 | 0,390 | 0,23 | 0 | 0,02 |  | 0,01 | 0,04 | 3 A | Suspec Corrosive |
|  | 10 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10 | 07/12/2017 |  |  | 3.622 | 5 | 7 | 0 | 1.165 | 0,000 | 0,170 | 0,23 | 0 | 0,00 |  | 0,01 | 0,08 | 2C | Non corrosive |
| 8 | 11 | 04/07/17 | Trafo 1 ESP | 3 | 1.243 | 0 | 0 | 0 | 79 | 0,000 | 0,350 | 0,00 | 0 | 0,01 |  | 0,01 | 0,00 | 1 B | Non corrosive |
|  | 11 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 11 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 11 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 11 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 11 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 11 | 07/12/2017 |  |  | 612 | 0 | 0 | 0 | 83 | 0,000 | 0,040 | 0,18 | 0 | .01 |  | 0,00 | 0,00 | 2E | Non corrosive |
| 9 | 12 | 04/07/17 | Trafo 2 ESP | 3 | 2.431 | 3 | 5 | 0 | 180 | 0,000 | 1,330 | 0,00 | 169 | 0,00 |  | 0,01 | 0,01 | 2 C | Non corrosive |
|  | 12 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12 | 07/12/2017 |  |  | 912 | 0 | 0 | 0 | 147 | 0,000 | 0,030 | 0,20 | 0 | 0,00 |  | 0,00 | 0,00 | 3A | Non corrosive |
| 10 | 13 | 04/07/17 | Trafo 3 ESP | 3 | 1.068 | 0 | 0 | 0 | 62 | 0,000 | 0,620 | 0,01 | 0 | 0,00 |  | 0,01 | 0,00 | 2 C | Non corrosive |
|  | 13 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 13 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 13 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 13 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 13 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 13 | 07/12/2017 |  |  | 559 | 0 | 0 | 0 | 57 | 0,000 | .08 | .21 | 0 | 0,00 |  | 0,00 | 0,00 | 2E | Non corrosive |
| 11 | 14 | 04/07/17 | Trafo 4 ESP | 3 | 665 | 0 | 0 | 0 | 37 | 0,000 | 1,360 | 0,01 | 0 | 0,00 |  | 0,00 | 0,00 | 3 A | Suspec Corrosive |
|  | 14 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 14 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 14 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 14 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 14 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 14 | 07/12/2017 |  |  | 675 | 0 | 0 | 0 | 38 | 0,000 | 0,370 | 0,03 | 0 | 0,00 |  | 0,00 | 0,00 | 1B | Non corrosive |
| 12 | 15 | 04/07/17 | Ash Handling |  | 5.037 | 7 | 8 | 0 | 511 | 0,000 | 0,730 | 0,23 | 0 | 0,00 |  | 0,01 | 0,01 | 1 B | Non corrosive |
|  | 15 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 | 07/12/2017 |  |  | 5.440 | 8 | 9 | 0 | 644 | 0,000 | 0,240 | 0,24 | 0 | 0,00 |  | 0,00 | 0,01 | 2C | Non corrosive |

| no | Test Cer. | Date Test | st laboratorium cennix |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | nama unit D3612 |  |  |  |  |  |  | lpf (C) |  | dbpc | furan |  | metal in oil |  |  | corr. sul | keterangan |
|  |  |  |  |  | CO2 | C2H6 | C2H4 | C2H2 | TOT | 25O | 100O |  |  | Al |  | Fe | Cu |  |  |
|  |  | Standa |  |  | carbon r dioksida | ethane | ethylene | acethylene |  | ASTM D924 |  | ASTM D2668 | ASTM D5837 |  | ASTM D3635 |  |  | ASTM D1275B |  |
|  |  |  |  |  | < 2.500 | < 65 | <50 | < 2 | < 687 | < 0.1 | < 2.9 | > .2 | < 100 | 0,00 |  | 0,00 | 0,00 |  | Non corrosive |
| 13 | 16 | 04/07/17 | Ash Handling |  | 1.676 | 0 | 1 | 0 | 152 | 0,000 | 1,350 | 0,22 | 0 | 0,00 |  | 0,01 | 0,00 | 3 A | Suspec Corrosive |
|  | 16 | 30/07/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 16 | 30/08/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 16 | 29/09/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 16 | 30/10/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 16 | 27/11/2017 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 16 | 07/12/2017 |  |  | 2.783 | 0 | 4 | 0 | 304 | 0,000 | 0,270 | 0,24 | 3 | 0,00 |  | 0,00 | 0,01 | 1A | Non corrosive |

| no | Test Cer. | Date Test | nama unit |  | MALAYSIAN LAB RECOMMENDATION r | PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- |
| Standa |  |  |  |  |  |  |
| 1 | 1 | 27/02/17 | Main trafo | 1 | Retest 6 months: DGA Check leakages Other parameters: Periodic Condition Monitoring | FOR TEST 07 DECEMBER 2017 Untuk Main Trafo 1 dan 3 serta Trafo UAT 3 yang tinggi CO dan CO2 nya, harap diperhatikan masalah cooling system antara lain menyalakan fan sejak awal trafo dinyalakan. Salah satu akibat dari CO dan CO2 yang tinggi (yang artinya sedang mengalami gangguan thermal secara internal) Mengingat banyak trafo ESP (Tc 5,6,7,8,11,12,13) yang kurang memenuhi syarat. Kami sarankan untuk diganti minyak saja. Selain jumlah minyaknya sedikit biaya juga akan jauh lebih murah, Saran |
|  | 4 | 04/07/17 |  |  | Retest 6 months: DGA Add inhibitor 2,6-DBPC and Passivator Other parameters: Periodic Condition Monitoring |  |
|  | 4 | 30/07/2017 |  |  | Periodic condition monitoring |  |
|  | 4 | 30/08/2017 |  |  | Periodic condition monitoring |  |
|  | 4 | 29/09/2017 |  |  | Periodic condition monitoring |  |
|  | 4 | 30/10/2017 |  |  | Periodic condition monitoring |  |
|  | 4 | 27/11/2017 |  |  | Periodic condition monitoring |  |
|  | 4 | 07/12/2017 |  |  | Retest 6 mnth : DGA |  |
| 2 | 5 | 04/07/17 | Trafo 1 ESP | 1 | Perform OIL REGENERATION | kami saat penggantian minyak melalui purifikasi dengan temperatur lebih dari 650C dan vacuum diatas 74 CMHg diatas 7 cycle Trafo ESP (Tc 6,7,8) Furan (FOL) banyak berkurang karena moisture cukup banyak dalam kertas dan kemungkinan juga kualitas kertas kurang bagus |
|  | 5 | 30/07/2017 |  |  | Perform OIL REGENERATION |  |
|  | 5 | 30/08/2017 |  |  | Perform OIL REGENERATION |  |
|  | 5 | 29/09/2017 |  |  | Perform OIL REGENERATION |  |
|  | 5 | 30/10/2017 |  |  | Perform OIL REGENERATION |  |
|  | 5 | 27/11/2017 |  |  | Perform OIL REGENERATION |  |
|  | 5 | 07/12/2017 |  |  | Perform OIL REGENERATION |  |
| 3 | 6 | 04/07/17 | Trafo 2 ESP | 1 | Perform OIL REGENERATION | Untuk trafo Ash Handling sebaiknya segera dipurifikasi juga |
|  | 6 | 30/07/2017 |  |  | Perform OIL REGENERATION | dengan temperatur diats 650c dan vacuum diatas 74 CMHg sekitar |
|  | 6 | 30/08/2017 |  |  | Perform OIL REGENERATION | >7 cycle |
|  | 6 | 29/09/2017 |  |  | Perform OIL REGENERATION |  |
|  | 6 | 30/10/2017 |  |  | Perform OIL REGENERATION | FOR TEST 27 NOVEMBER 2017 |
|  | 6 | 27/11/2017 |  |  | Perform OIL REGENERATION |  |
|  | 6 | 07/12/2017 |  |  | Perform OIL REGENERATION | Keadaan masih relatif tidak berubah dibandingkan dengan hasil test |
| 4 | 7 | 04/07/17 | Trafo 3 ESP | 1 | Retest 6 months: Acidity, IFT, LPF, Diel and Water Content Add inhibitor 2,6-DBPC and Passivator Other parameters: Periodic Condition Monitoring | pada bulan yang sebelumnya. Jadi rekomendasi saya masih sama seperti yang bulan lalu, FOR TEST 30 OKTOBER 2017 Keadaan masih relatif tidak berubah dibandingkan dengan hasil test pada bulan yang sebelumnya. Jadi rekomendasi saya masih sama seperti yang bulan lalu, |
|  | 7 | 30/07/2017 |  |  | Retest 6 months: Acidity, IFT and Liquid Power Factor Other parameters: Periodic Condition Monitoring |  |
|  | 7 | 30/08/2017 |  |  | Periodic condition monitoring |  |
|  | 7 | 29/09/2017 |  |  | Periodic condition monitoring |  |
|  | 7 | 30/10/2017 |  |  | Periodic condition monitoring |  |
|  | 7 | 27/11/2017 |  |  | Periodic condition monitoring |  |
|  | 7 | 07/12/2017 |  |  | Retest 6 months: Acidity, IFT |  |
| 5 | 8 | 04/07/17 | Trafo 4 ESP | 1 | Perform OIL REGENERATION Inspect silica gel | FOR TEST 29 SEssdsdsdsdsdsdsddsdsddsPTEMBER |
|  |  |  |  |  |  | 2017 |
|  | 8 | 30/07/2017 |  |  | Perform OIL REGENERATION |  |
|  | 8 | 30/08/2017 |  |  | Perform OIL REGENERATION |  |
|  | 8 | 29/09/2017 |  |  | Perform OIL REGENERATION | Yang perlu diganti minyak hanyalah Tc 12. Karena minyak |
|  | 8 | 30/10/2017 |  |  | Perform OIL REGENERATION | sedikit, jauh lebih murah dibanding regenerasi. |
|  | 8 | 27/11/2017 |  |  | Perform OIL REGENERATION |  |
|  | 8 | 07/12/2017 |  |  | Perform OIL REGENERATION | Yang perlu dipurifikasi adalah Tc 5, 6,11, 14, 16. |
| 6 | 2 | 27/02/17 | Main trafo | 3 | Retest 6 months: DGA | Mengingat banyak trafo ESP (Tc 5,6,7,8,11,12,13,14) yang kurang memenuhi syarat. Kami sarankan untuk diganti minyak saja. Selain jumlah minyaknya sedikit biaya juga akan jauh lebih murah, Saran kami sat penggantian minyak melalui purifikasi dengan temperatur lebih dari 650C dan vacuum diatas 74 CMHg pelaksanaan diatas 7 cycle. Dari hasil terakhir nampak perubahan moisture pada isoilasi |
|  |  |  |  |  | Other parameters: Periodic Condition Monitoring |  |
|  | 9 | 04/07/17 |  |  | Add Passivator |  |
|  |  |  |  |  | Periodic Condition Monitoring |  |
|  | 9 | 30/07/2017 |  |  | Periodic condition monitoring |  |
|  | 9 | 30/08/2017 |  |  | Periodic condition monitoring |  |
|  | 9 | 29/09/2017 |  |  | Periodic condition monitoring |  |
|  | 9 | 30/10/2017 |  |  | Periodic condition monitoring |  |

| no | Test Cer. | Date Test | nama unit |  | MALAYSIAN LAB RECOMMENDATION r | PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- |
| Standa |  |  |  |  |  |  |
|  |  |  |  |  |  | Dari hasil terakhir nampak perubahan moisture pada isoilasi |
|  | 9 | 27/11/2017 |  |  | Periodic condition monitoring | ("Grade") pada trafo2 ESP naik turun ini menandakan isolasi sudah mulai kurang bagus. |
|  | 9 | 07/12/2017 |  |  | Periodic condition monitoring |  |
| 7 | 3 | 27/02/17 | Trafo UAT | 3 | Retest 6 months: DGA Other parameters: Periodic Condition Monitoring |  |
|  | 10 | 04/07/17 |  |  | Add Passivator Periodic Condition Monitoring Inspect silica gel | FOR TEST 30 AUGUST 2017 |
|  |  |  |  |  |  | Mengingat banyak trafo ESP (Tc 5,6,7,8,11,12,13,14) yang kurang |
|  |  |  |  |  |  | memenuhi syarat. Kami sarankan untuk diganti minyak saja. Selain |
|  | 10 | 30/07/2017 |  |  | Periodic condition monitoring | jumlah minyaknya sedikit biaya juga akan jauh lebih murah, Saran |
|  | 10 | 30/08/2017 |  |  | Periodic condition monitoring | kami sat penggantian minyak melalui purifikasi dengan temperatur |
|  | 10 | 29/09/2017 |  |  | Periodic condition monitoring | lebih dari 650C dan vacuum diatas 74 CMHg pelaksanaan diatas 7 |
|  | 10 | 30/10/2017 |  |  | Periodic condition monitoring | cycle |
|  | 10 | 27/11/2017 |  |  | Periodic condition monitoring |  |
|  | 10 | 07/12/2017 |  |  | Periodic condition monitoring | Dari hasil terakhir nampak perubahan moisture pada isoilasi ("Grade") pada trafo2 ESP naik turun ini menandakan isolasi kurang |
| 8 | 11 | 04/07/17 | Trafo 1 ESP | 3 | Perform OIL REGENERATION | bagus. FOR TEST 30 JULY 2017 Untuk trafo ESP 2 Unit 3 sebaiknya minyaknya segera diganti saja, karena Acidity dan Grade Water Content sudah sangat di luar |
|  | 11 | 30/07/2017 |  |  | Perform OIL REGENERATION |  |
|  | 11 | 30/08/2017 |  |  | Perform OIL REGENERATION |  |
|  | 11 | 29/09/2017 |  |  | Perform OIL REGENERATION |  |
|  | 11 | 30/10/2017 |  |  | Perform OIL REGENERATION |  |
|  | 11 | 27/11/2017 |  |  | Perform OIL REGENERATION |  |
|  | 11 | 07/12/2017 |  |  | Perform OIL PURIFICATION |  |
| 9 | 12 | 04/07/17 | Trafo 2 ESP | 3 | Perform OIL REGENERATION | standard |
|  | 12 | 30/07/2017 |  |  | Perform OIL REGENERATION |  |
|  | 12 | 30/08/2017 |  |  | Perform OIL REGENERATION | Untuk trafo Ash Handling, segera dipurifikasi karena water content |
|  | 12 | 29/09/2017 |  |  | Perform OIL REGENERATION | sudah jauh di atas standard. |
|  | 12 | 30/10/2017 |  |  | Perform OIL REGENERATION |  |
|  | 12 | 27/11/2017 |  |  | Perform OIL REGENERATION |  |
|  | 12 | 07/12/2017 |  |  | Perform OIL REGENERATION |  |
| 10 | 13 | 04/07/17 | Trafo 3 ESP | 3 | Perform OIL REGENERATION | FOR TEST 04 JULY 2017 Untuk Main Trafo 1 dan 3 serta Trafo UAT 3 yang tinggi CO dan CO2 nya, harap diperhatikan masalah cooling system antara lain menyalakan fan sejak awal trafo dinyalakan. Salah satu akibat dari CO dan CO2 yang tinggi (yang artinya sedang mengalami gangguan thermal secara internal) adalah penurunan kondisi Corrosive Sulphur. Dari data yang ada, pada bulan February yang lalu, masih |
|  | 13 | 30/07/2017 |  |  | Perform OIL REGENERATION |  |
|  | 13 | 30/08/2017 |  |  | Perform OIL REGENERATION |  |
|  | 13 | 29/09/2017 |  |  | Perform OIL REGENERATION |  |
|  | 13 | 30/10/2017 |  |  | Perform OIL REGENERATION |  |
|  | 13 | 27/11/2017 |  |  | Perform OIL REGENERATION |  |
|  | 13 | 07/12/2017 |  |  | Perform OIL PURIFICATION |  |
| 11 | 14 | 04/07/17 | Trafo 4 ESP | 3 | Retest 6 months: Acidity, IFT and LPF Add inhibitor 2,6-DBPC and Passivator Other parameters: Periodic Condition Monitoring | "Non Corrosive", dan pada bulan Juli ini menjadi "Suspec Corrosive". |
|  |  |  |  |  |  | Mengingat banyak trafo ESP (Tc 5,6,7,8,11,12,13) yang kurang |
|  | 14 | 30/07/2017 |  |  | Retest 6 months: Acidity, IFT and Liquid Power Factor Other parameters: Periodic Condition Monitoring | memenuhi syarat. Kami sarankan untuk diganti minyak saja. |
|  |  |  |  |  |  | Selain jumlah minyaknya sedikit biaya juga akan jauh lebih murah, |
|  | 14 | 30/08/2017 |  |  | Periodic condition monitoring | Saran kami saat penggantian minyak melalui purifikasi dengan 0 |
|  | 14 | 29/09/2017 |  |  | Periodic condition monitoring | temperatur lebih dari 65 C dan vacuum diatas 74 CMHg diatas 7 |
|  | 14 | 30/10/2017 |  |  | Periodic condition monitoring | cycle |
|  | 14 | 27/11/2017 |  |  | Periodic condition monitoring |  |
|  | 14 | 07/12/2017 |  |  | Retest 6 months: Acidity, IFT | Trafo ESP (Tc 6,7,8) Furan (FOL) banyak berkurang karena |
| 12 | 15 | 04/07/17 | Ash Handling |  | Add Passivator Periodic Condition Monitoring | moisture cukup banyak dalam kertas dan kemungkinan juga kualitas kertas kurang bagus Untuk trafo Ash Handling sebaiknya segera dipurifikasi juga dengan temperatur diats 650c dan vacuum diatas 74 CMHg sekitar >7 cycle |
|  | 15 | 30/07/2017 |  |  | Periodic condition monitoring |  |
|  | 15 | 30/08/2017 |  |  | Periodic condition monitoring |  |
|  | 15 | 29/09/2017 |  |  | Periodic condition monitoring |  |
|  | 15 | 30/10/2017 |  |  | Periodic condition monitoring |  |
|  | 15 | 27/11/2017 |  |  | Periodic condition monitoring |  |
|  | 15 | 07/12/2017 |  |  | Periodic condition monitoring |  |

| no | Test Cer. | Date Test | nama unit |  | MALAYSIAN LAB RECOMMENDATION r | PAK SOETJAHJONO (TXM ADVISOR) RECOMMENDATION |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Standa |  |  |  |  |
| 13 | 16 | 04/07/17 | Ash Handling |  | Add Passivator Periodic Condition Monitoring |  |
|  | 16 | 30/07/2017 |  |  | Retest 6 months: Dielectric and Water Content Other parameters: Periodic Condition Monitoring |  |
|  | 16 | 30/08/2017 |  |  | Periodic Condition Monitoring |  |
|  | 16 | 29/09/2017 |  |  | Retest 6 months: Dielectric and Water Content |  |
|  | 16 | 30/10/2017 |  |  | Retest 6 months: Dielectric and Water Content Periodic Condition Monitoring |  |
|  | 16 | 27/11/2017 |  |  |  |  |
|  | 16 | 07/12/2017 |  |  | Perform OIL PURIFICATION |  |

Summary by Soetjahjono

TxM Indonesia