ALL TEST 6.31 Analysis Results

#### Performance Summary

# Bottom Line

This induction motor is operating normally, no action is required.

This induction motor  exhibits suspicious operation, trending of the induction motor  is warranted.

X	This induction motor  exhibits abnormal indications, action is warranted, NOW.

# Power Factor Commentary

X	Power factor exceeds 0.85.

Power factor is below 0.85, see detailed report.

# Current Commentary

Current variation is within normal limits.

X	Current variation is beyond normal limits, see detailed report.

# Voltage Commentary

X	Voltage variation is within normal limits.

Voltage variation is beyond normal limits, see detailed report.

RMS voltage differs from nameplate by more than 5%.

# Load Commentary

X	Load on the induction motor  is consistent with nameplate values.

Load on the induction motor  exceeds nameplate values, see detailed report.

Load on the induction motor  is less than 25%.

# Phase Connection Commentary

X	Connections are normal.

Voltage ground reference is NOT neutral.

Loose connection.

# Rotor Commentary

X	Rotor bar health is normal.

Rotor bar health is questionable, see detailed report.

Load is insufficient to determine rotor bar health, at this time.

# Stator Commentary

X	Stator health is normal.

Stator mechanical health is questionable. .

Turn to turn short.

# Rotor/Stator Air-gap Characteristics

X	Dynamic or static eccentricity indications do not exist.

Indications of static eccentricity exist .

Indications of dynamic eccentricity exist.

# Harmonic Distortion Commentary

X	There is no evidence of harmonic distortion.

There is evidence of harmonic distortion, see detailed report.

# Misalignment Indications

X	There are no indications of mechanical problems like misalignment or  unbalance.

There are indications of mechanical problems like misalignment / unbalance.  Perform vibr. survey to identify and correct the cause.

INPUT SUMMARY

# NAMEPLATE INFORMATION

|  |  | Units |
| --- | --- | --- |
| Model Number | Y2 - 280-4 |  |
| Tested Equipment | Induction |  |
| Power | 100.54 | HP |
| RPM | 980.0 | Rpm |
| Poles | 6 |  |
| Phases: | 3 |  |
| Voltage | 380.0 | Volt |
| Full Load Current | 139.60 | Amp |
| No Load Current | 3.00 | Amp |
| Number of rotor bars | 80 |  |
| Number of stator slots | -1 |  |
| Torque | 538.6 | Ft.Lb |
| CT Ratio | 1.000 |  |
| Service Factor | 115 |  |
| Motor efficiency | -1.000 |  |
| Power factor | 0.870 |  |

Description:

Belum ada data rotor bar dan stator slot

| LEGENDS: |  |
| --- | --- |
| Impedance | = Complex Impedance = vi/ci |
| CF | = Crest Factor = (waveform peak)/(waveform rms) |
| VDF | = Transformer Harmonic De-rating Factor = sqrt(2)/CF, % |

| Slip % | = SRSS sum of slip and harmonic "levels" divided by RMS level of RMS DEMOD spectra between 0 and 65 Hz. |
| --- | --- |
| Upper sb | = dB level of upper slip sideband of power line peak |
| Lower sb | = dB level of lower slip sideband of power line peak |
| Se, fund | = Location of pole pass frequency fundamental, Hz |
| Se, harm | = Number of pole pass frequency harmonics |
| Rotor bar health | = Estimate of the percent of broken or cracked rotor bars |
| RB Hlt Index | = Rotor bar health index |

| THDF | = Voltage De-rating Factor = 100 - (voltage unbalance, %)^2, % |
| --- | --- |
| Level | = Sum of spectral amplitudes of pole pass frequency fundamentals and harmonics |
| Thd | = Total harmonic distortion |
| +Ve | = Positive sequence harmonic |
| -Ve | = Negative sequence harmonic |
| Zero | = Zero sequence harmonic |

Detailed Calculations

Running Speed	= 15.533 Hz [932 RPM]

Pole pass frequency	= 6.927 Hz [416 RPM]

Load	= 46.9 %

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Current 1 | 57.180 | 83.809 | 1.466 |
| Current 2 | 59.400 | 87.063 | 1.466 |
| Current 3 | 51.210 | 75.059 | 1.466 |
| Average | 55.930 | 81.977 | 1.466 |
| % dev | 8.4 | 8.4 | 0.0 |

THDF = 96.5

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Voltage 1 | 390.900 | 559.400 | 1.431 |
| Voltage 2 | 390.900 | 559.400 | 1.431 |
| Voltage 3 | 390.700 | 559.110 | 1.431 |
| Average | 390.830 | 559.300 | 1.431 |
| % dev | 0.0 | 0.0 | 0.0 |

VDF = 100.0

* Note-

Phase 2 and 3 CF and peak entries are assumed to be the same as phase-1.

|  |  |  | App. Power | Real Power | Reac. Power |
| --- | --- | --- | --- | --- | --- |
|  | Power factor | Impedance | kVA | kW | kVARS |
| Phase 1 | 0.994 | 6.836 | 12.894 | 12.814 | 1.435 |
| Phase 2 | 0.995 | 6.581 | 13.401 | 13.335 | 1.325 |
| Phase 3 | 0.999 | 7.629 | 11.553 | 11.546 | 0.401 |
| Avg/Total | 0.996 | 7.015 | 37.848 | 37.695 | 3.161 |
| % dev | 0.3 | 8.8 |  |  |  |

Demand Pwr = 50.53 HP

Load:46.9 %

Motor Eff.:91.9 %

Loss due to THD:

Output Pow.:28.26 KW

Output Trq.:213.36 Ft.Lb

| Summary of Rotor Bar Health |  |  |  |  | Power line dB diff. |  | RB Hlt Index |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Se, fund |  | Se, harm | Level % | Upper SB | Lower SB |  |
| Measured | 6.927 |  | 2 | 0.1 | -59.667 | -57.143 | 0.159 |
| Severity level |  | Rotor Condition Assessment |  |  | #### Recommended Corrective Action |  |  |
| 1 |  | Excellent |  |  | None |  |  |

| Harmonic Distortion Results: Voltage input, from 50.018 Hz harmonics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | THD Odd % | THD Even % | +ve% | -ve % | Zero % | THD All % |
| #### Current 1 | 0.699 | 0.110 | 0.263 | 0.587 | 0.296 | 0.708 |
| Current 2 | *** | *** | *** | *** | *** | *** |
| Current 3 | *** | *** | *** | *** | *** | *** |
| Voltage 1 | 0.748 | 0.053 | 0.196 | 0.717 | 0.097 | 0.750 |
| Voltage 2 | *** | *** | *** | *** | *** | *** |
| Voltage 3 | *** | *** | *** | *** | *** | *** |

| Harmonic distortion table – Peak values, voltage is phase to ground |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Hz | Cur1 | Vlt1 | Cur2 | Vlt2 | Cur3 | Vlt3 |
| 3000 | 79.9 | 315 | *** | *** | *** | *** |
| 6000 | 0.1 | 0 | *** | *** | *** | *** |
| 9000 | 0.2 | 0 | *** | *** | *** | *** |
| 12000 | 0.0 | 0 | *** | *** | *** | *** |
| 15000 | 0.5 | 2 | *** | *** | *** | *** |
| 18000 | 0.0 | 0 | *** | *** | *** | *** |
| 21000 | 0.2 | 1 | *** | *** | *** | *** |
| 24000 | 0.0 | 0 | *** | *** | *** | *** |
| 27000 | 0.0 | 0 | *** | *** | *** | *** |
| 30000 | 0.0 | 0 | *** | *** | *** | *** |
| 33000 | 0.1 | 0 | *** | *** | *** | *** |
| 36000 | 0.0 | 0 | *** | *** | *** | *** |

Figure 1: Current harmonic distortion plot

Figure 2: Voltage harmonic distortion plot

Figure 3: Raw Current

Figure 4: Raw Current Frequency spectrum

Figure 5: Raw Voltage

Figure 6: Raw Voltage Frequency spectrum

Figure 7: Demodulated current trace

Figure 8: Raw current spectrum

Figure 9: Demodulated current spectrum