ALL TEST 6.31 Analysis Results

#### Performance Summary

# Bottom Line

This induction motor is operating normally, no action is required.

This induction motor  exhibits suspicious operation, trending of the induction motor  is warranted.

X	This induction motor  exhibits abnormal indications, action is warranted, NOW.

# Power Factor Commentary

Power factor exceeds 0.85.

X	Power factor is below 0.85, see detailed report.

# Current Commentary

X	Current variation is within normal limits.

Current variation is beyond normal limits, see detailed report.

# Voltage Commentary

Voltage variation is within normal limits.

Voltage variation is beyond normal limits, see detailed report.

X	RMS voltage differs from nameplate by more than 5%.

# Load Commentary

Load on the induction motor  is consistent with nameplate values.

Load on the induction motor  exceeds nameplate values, see detailed report.

X	Load on the induction motor  is less than 25%.

# Phase Connection Commentary

X	Connections are normal.

Voltage ground reference is NOT neutral.

Loose connection.

# Rotor Commentary

Rotor bar health is normal.

Rotor bar health is questionable, see detailed report.

X	Load is insufficient to determine rotor bar health, at this time.

# Stator Commentary

X	Stator health is normal.

Stator mechanical health is questionable. .

Turn to turn short.

# Rotor/Stator Air-gap Characteristics

X	Dynamic or static eccentricity indications do not exist.

Indications of static eccentricity exist .

Indications of dynamic eccentricity exist.

# Harmonic Distortion Commentary

X	There is no evidence of harmonic distortion.

There is evidence of harmonic distortion, see detailed report.

# Misalignment Indications

X	There are no indications of mechanical problems like misalignment or  unbalance.

There are indications of mechanical problems like misalignment / unbalance.  Perform vibr. survey to identify and correct the cause.

INPUT SUMMARY

# NAMEPLATE INFORMATION

|  |  | Units |
| --- | --- | --- |
| Serial Number | JB/18680-2008 |  |
| Model Number | Y2-250-6 |  |
| Tested Equipment | Induction |  |
| Power | 49.60 | HP |
| RPM | 980.0 | Rpm |
| Poles | 6 |  |
| Phases: | 3 |  |
| Voltage | 380.0 | Volt |
| Full Load Current | 70.70 | Amp |
| No Load Current | 3.00 | Amp |
| Number of rotor bars | 58 |  |
| Number of stator slots | -1 |  |
| Torque | 265.7 | Ft.Lb |
| CT Ratio | 1.000 |  |
| Service Factor | 115 |  |
| Motor efficiency | -1.000 |  |
| Power factor | 0.860 |  |

Description:

Belum ada data rotor bar dan stator slot

| LEGENDS: |  |
| --- | --- |
| Impedance | = Complex Impedance = vi/ci |
| CF | = Crest Factor = (waveform peak)/(waveform rms) |
| VDF | = Transformer Harmonic De-rating Factor = sqrt(2)/CF, % |

| Slip % | = SRSS sum of slip and harmonic "levels" divided by RMS level of RMS DEMOD spectra between 0 and 65 Hz. |
| --- | --- |
| Upper sb | = dB level of upper slip sideband of power line peak |
| Lower sb | = dB level of lower slip sideband of power line peak |
| Se, fund | = Location of pole pass frequency fundamental, Hz |
| Se, harm | = Number of pole pass frequency harmonics |
| Rotor bar health | = Estimate of the percent of broken or cracked rotor bars |
| RB Hlt Index | = Rotor bar health index |

| THDF | = Voltage De-rating Factor = 100 - (voltage unbalance, %)^2, % |
| --- | --- |
| Level | = Sum of spectral amplitudes of pole pass frequency fundamentals and harmonics |
| Thd | = Total harmonic distortion |
| +Ve | = Positive sequence harmonic |
| -Ve | = Negative sequence harmonic |
| Zero | = Zero sequence harmonic |

Detailed Calculations

Running Speed	= 16.479 Hz [989 RPM]

Pole pass frequency	= 0.984 Hz [59 RPM]

Load	= 0.0 %

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Current 1 | 51.590 | 74.030 | 1.435 |
| Current 2 | 51.040 | 71.894 | 1.409 |
| Current 3 | 51.390 | 72.816 | 1.417 |
| Average | 51.340 | 72.913 | 1.420 |
| % dev | 0.6 | 1.5 | 1.0 |

THDF = 99.6

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Voltage 1 | 0.000 | 0.000 | 1.000 |
| Voltage 2 | 0.000 | 0.000 | 1.000 |
| Voltage 3 | 0.000 | 0.000 | 1.000 |
| Average | 0.000 | 0.000 | 1.000 |

|  |  |  | App. Power | Real Power | Reac. Power |
| --- | --- | --- | --- | --- | --- |
|  | Power factor | Impedance | kVA | kW | kVARS |
| Phase 1 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| Phase 2 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| Phase 3 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| Avg/Total | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |

Demand Pwr = 0.00 HP

| Summary of Rotor Bar Health |  |  |  |  | Power line dB diff. |  | RB Hlt Index |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Se, fund |  | Se, harm | Level % | Upper SB | Lower SB |  |
| Measured | 0.984 |  | 0 | 0.0 | -72.104 | -70.268 | - |
| Severity level |  | Rotor Condition Assessment |  |  | #### Recommended Corrective Action |  |  |
| - |  | Load too low for determination |  |  | - |  |  |

| Harmonic Distortion Results: Voltage input, from 50.049 Hz harmonics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | THD Odd % | THD Even % | +ve% | -ve % | Zero % | THD All % |
| #### Current 1 | 0.634 | 0.272 | 0.219 | 0.602 | 0.255 | 0.690 |
| Current 2 | *** | *** | *** | *** | *** | 0.000 |
| Current 3 | *** | *** | *** | *** | *** | 0.000 |
| Voltage 1 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| Voltage 2 | *** | *** | *** | *** | *** | 0.000 |
| Voltage 3 | *** | *** | *** | *** | *** | 0.000 |

| Harmonic distortion table – Peak values, voltage is phase to ground |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Hz | Cur1 | Vlt1 | Cur2 | Vlt2 | Cur3 | Vlt3 |
| 3000 | 73.3 | 0 | *** | *** | *** | *** |
| 6000 | 0.2 | 0 | *** | *** | *** | *** |
| 9000 | 0.2 | 0 | *** | *** | *** | *** |
| 12000 | 0.1 | 0 | *** | *** | *** | *** |
| 15000 | 0.4 | 0 | *** | *** | *** | *** |
| 18000 | 0.0 | 0 | *** | *** | *** | *** |
| 21000 | 0.1 | 0 | *** | *** | *** | *** |
| 24000 | 0.0 | 0 | *** | *** | *** | *** |
| 27000 | 0.0 | 0 | *** | *** | *** | *** |
| 30000 | 0.0 | 0 | *** | *** | *** | *** |
| 33000 | 0.1 | 0 | *** | *** | *** | *** |
| 36000 | 0.0 | 0 | *** | *** | *** | *** |

Figure 1: Current harmonic distortion plot

Figure 2: Voltage harmonic distortion plot

Figure 3: Raw Current

Figure 4: Raw Current Frequency spectrum

Figure 5: Raw Voltage

Figure 6: Raw Voltage Frequency spectrum

Figure 7: Demodulated current trace

Figure 8: Raw current spectrum

Figure 9: Demodulated current spectrum