ALL TEST 6.31 Analysis Results

#### Performance Summary

# Bottom Line

This induction motor is operating normally, no action is required.

This induction motor  exhibits suspicious operation, trending of the induction motor  is warranted.

X	This induction motor  exhibits abnormal indications, action is warranted, NOW.

# Power Factor Commentary

X	Power factor exceeds 0.85.

Power factor is below 0.85, see detailed report.

# Current Commentary

X	Current variation is within normal limits.

Current variation is beyond normal limits, see detailed report.

# Voltage Commentary

Voltage variation is within normal limits.

X	Voltage variation is beyond normal limits, see detailed report.

X	RMS voltage differs from nameplate by more than 5%.

# Load Commentary

X	Load on the induction motor  is consistent with nameplate values.

Load on the induction motor  exceeds nameplate values, see detailed report.

Load on the induction motor  is less than 25%.

# Phase Connection Commentary

Connections are normal.

X	Voltage ground reference is NOT neutral.

Loose connection.

# Rotor Commentary

X	Rotor bar health is normal.

Rotor bar health is questionable, see detailed report.

Load is insufficient to determine rotor bar health, at this time.

# Stator Commentary

X	Stator health is normal.

Stator mechanical health is questionable. .

Turn to turn short.

# Rotor/Stator Air-gap Characteristics

X	Dynamic or static eccentricity indications do not exist.

Indications of static eccentricity exist .

Indications of dynamic eccentricity exist.

# Harmonic Distortion Commentary

X	There is no evidence of harmonic distortion.

There is evidence of harmonic distortion, see detailed report.

# Misalignment Indications

X	There are no indications of mechanical problems like misalignment or  unbalance.

There are indications of mechanical problems like misalignment / unbalance.  Perform vibr. survey to identify and correct the cause.

# Bearing Commentary

X	There is no evidence of bearing problem.

Indications of potential bearing problems, perform vibration survey to verify.

INPUT SUMMARY

# NAMEPLATE INFORMATION

|  |  | Units |
| --- | --- | --- |
| Manufacturer | JIANGSU QINGJIA |  |
| Serial Number | K4000045-0701 |  |
| Model Number | YKK4003-4 |  |
| Tested Equipment | Induction |  |
| Power | 475.87 | HP |
| RPM | 1480.0 | Rpm |
| Poles | 4 |  |
| Phases: | 3 |  |
| Voltage | 6300.0 | Volt |
| Full Load Current | 40.50 | Amp |
| No Load Current | 3.00 | Amp |
| Number of rotor bars | -1 |  |
| Number of stator slots | -1 |  |
| Torque | 1688.1 | Ft.Lb |
| CT Ratio | 15.000 |  |
| PT Ratio | 60.000 |  |
| Duty Cycle | S1 |  |
| Service Factor | 115 |  |
| Insulation Type | F |  |
| Motor efficiency | -1.000 |  |
| Power factor | -1.000 |  |

Description:

Belum ada data rotor bar dan stator slot

| LEGENDS: |  |
| --- | --- |
| Impedance | = Complex Impedance = vi/ci |
| CF | = Crest Factor = (waveform peak)/(waveform rms) |
| VDF | = Transformer Harmonic De-rating Factor = sqrt(2)/CF, % |

| Slip % | = SRSS sum of slip and harmonic "levels" divided by RMS level of RMS DEMOD spectra between 0 and 65 Hz. |
| --- | --- |
| Upper sb | = dB level of upper slip sideband of power line peak |
| Lower sb | = dB level of lower slip sideband of power line peak |
| Se, fund | = Location of pole pass frequency fundamental, Hz |
| Se, harm | = Number of pole pass frequency harmonics |
| Rotor bar health | = Estimate of the percent of broken or cracked rotor bars |
| RB Hlt Index | = Rotor bar health index |

| THDF | = Voltage De-rating Factor = 100 - (voltage unbalance, %)^2, % |
| --- | --- |
| Level | = Sum of spectral amplitudes of pole pass frequency fundamentals and harmonics |
| Thd | = Total harmonic distortion |
| +Ve | = Positive sequence harmonic |
| -Ve | = Negative sequence harmonic |
| Zero | = Zero sequence harmonic |

Detailed Calculations

Running Speed	= 24.750 Hz [1485 RPM]

Pole pass frequency	= 1.099 Hz [66 RPM]

Load	= 44.7 %

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Current 1 | 27.000 | 39.411 | 1.460 |
| Current 2 | 27.300 | 38.670 | 1.416 |
| Current 3 | 27.300 | 39.120 | 1.433 |
| Average | 27.200 | 39.067 | 1.436 |
| % dev | 0.7 | 1.0 | 1.6 |

THDF = 98.5

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Voltage 1 | 6240.000 | 8864.000 | 1.421 |
| Voltage 2 | 3600.000 | 5231.800 | 1.453 |
| Voltage 3 | 3606.000 | 5054.700 | 1.402 |
| Average | 4482.000 | 6383.500 | 1.425 |
| % dev | 39.2 | 38.9 | 2.0 |

VDF = -1438.5

|  |  |  | App. Power | Real Power | Reac. Power |
| --- | --- | --- | --- | --- | --- |
|  | Power factor | Impedance | kVA | kW | kVARS |
| Phase 1 | 0.824 | 231.110 | 97.200 | 80.100 | 55.062 |
| Phase 2 | 0.888 | 131.870 | 98.280 | 87.300 | 45.141 |
| Phase 3 | 0.000 | 132.090 | 0.000 | 0.000 | 0.000 |
| Avg/Total | 1.712 | 165.020 | 195.480 | 167.400 | 100.200 |
| % dev | 0.0 | 40.0 |  |  |  |

Demand Pwr = 224.40 HP

Load:44.7 %

Motor Eff.:93.3 %

Loss due to THD:

Output Pow.:42.03 KW

Output Trq.:199.18 Ft.Lb

| Summary of Rotor Bar Health |  |  |  |  | Power line dB diff. |  | RB Hlt Index |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Se, fund |  | Se, harm | Level % | Upper SB | Lower SB |  |
| Measured | 1.099 |  | 1 | - | -66.202 | -60.756 | 0.053 |
| Severity level |  | Rotor Condition Assessment |  |  | #### Recommended Corrective Action |  |  |
| 1 |  | Excellent |  |  | None |  |  |

| Bearing condition |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Location | Bearing No. | IR | OR | T/C | BS |
| Drive end | SKF NU324 | OK | OK | OK | OK |
| Opposite end | SKF NU324 | OK | OK | OK | OK |

| Harmonic Distortion Results: Voltage input, from 50.049 Hz harmonics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | THD Odd % | THD Even % | +ve% | -ve % | Zero % | THD All % |
| #### Current 1 | 0.917 | 0.077 | 0.185 | 0.899 | 0.071 | 0.920 |
| Current 2 | *** | *** | *** | *** | *** | 0.000 |
| Current 3 | *** | *** | *** | *** | *** | 0.000 |
| Voltage 1 | 1.693 | 0.016 | 0.199 | 0.647 | 1.552 | 1.693 |
| Voltage 2 | *** | *** | *** | *** | *** | 0.000 |
| Voltage 3 | *** | *** | *** | *** | *** | 0.000 |

| Harmonic distortion table – Peak values, voltage is phase to ground |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Hz | Cur1 | Vlt1 | Cur2 | Vlt2 | Cur3 | Vlt3 |
| 50 | 39.3 | 5071 | *** | *** | *** | *** |
| 100 | 0.0 | 0 | *** | *** | *** | *** |
| 150 | 0.0 | 82 | *** | *** | *** | *** |
| 200 | 0.0 | 0 | *** | *** | *** | *** |
| 250 | 0.4 | 34 | *** | *** | *** | *** |
| 300 | 0.0 | 0 | *** | *** | *** | *** |
| 350 | 0.1 | 10 | *** | *** | *** | *** |
| 400 | 0.0 | 0 | *** | *** | *** | *** |
| 450 | 0.0 | 3 | *** | *** | *** | *** |
| 500 | 0.0 | 0 | *** | *** | *** | *** |
| 550 | 0.1 | 4 | *** | *** | *** | *** |
| 600 | 0.0 | 0 | *** | *** | *** | *** |

Figure 1: Current harmonic distortion plot

Figure 2: Voltage harmonic distortion plot

Figure 3: Raw Current

Figure 4: Raw Current Frequency spectrum

Figure 5: Raw Voltage

Figure 6: Raw Voltage Frequency spectrum

Figure 7: Demodulated current trace

Figure 8: Raw current spectrum

Figure 9: Demodulated current spectrum