ALL TEST 6.31 Analysis Results

#### Performance Summary

# Bottom Line

This induction motor is operating normally, no action is required.

X	This induction motor  exhibits suspicious operation, trending of the induction motor  is warranted.

This induction motor  exhibits abnormal indications, action is warranted, NOW.

# Power Factor Commentary

X	Power factor exceeds 0.85.

Power factor is below 0.85, see detailed report.

# Current Commentary

X	Current variation is within normal limits.

Current variation is beyond normal limits, see detailed report.

# Voltage Commentary

X	Voltage variation is within normal limits.

Voltage variation is beyond normal limits, see detailed report.

RMS voltage differs from nameplate by more than 5%.

# Load Commentary

X	Load on the induction motor  is consistent with nameplate values.

Load on the induction motor  exceeds nameplate values, see detailed report.

Load on the induction motor  is less than 25%.

# Phase Connection Commentary

X	Connections are normal.

Voltage ground reference is NOT neutral.

Loose connection.

# Rotor Commentary

X	Rotor bar health is normal.

Rotor bar health is questionable, see detailed report.

Load is insufficient to determine rotor bar health, at this time.

# Stator Commentary

X	Stator health is normal.

Stator mechanical health is questionable. .

Turn to turn short.

# Rotor/Stator Air-gap Characteristics

X	Dynamic or static eccentricity indications do not exist.

Indications of static eccentricity exist .

Indications of dynamic eccentricity exist.

# Harmonic Distortion Commentary

There is no evidence of harmonic distortion.

X	There is evidence of harmonic distortion, see detailed report.

# Bearing Commentary

X	There is no evidence of bearing problem.

Indications of potential bearing problems, perform vibration survey to verify.

INPUT SUMMARY

# NAMEPLATE INFORMATION

|  |  | Units |
| --- | --- | --- |
| Manufacturer | XIANGTAN ELECTR |  |
| Serial Number | YKK 5002-2 |  |
| Model Number | 87684 |  |
| Tested Equipment | Induction |  |
| Power | 1340.48 | HP |
| RPM | 2979.0 | Rpm |
| Poles | 2 |  |
| Phases: | 3 |  |
| Voltage | 6300.0 | Volt |
| Full Load Current | 109.20 | Amp |
| No Load Current | 3.00 | Amp |
| Number of rotor bars | -1 |  |
| Number of stator slots | -1 |  |
| Torque | 2362.4 | Ft.Lb |
| CT Ratio | 30.000 |  |
| PT Ratio | 60.000 |  |
| Service Factor | 115 |  |
| Frame Size | 50HZ |  |
| Motor efficiency | 0.000 |  |
| Power factor | 0.880 |  |

Description:

Belum ada data rotor bar dan stator slot

| LEGENDS: |  |
| --- | --- |
| Impedance | = Complex Impedance = vi/ci |
| CF | = Crest Factor = (waveform peak)/(waveform rms) |
| VDF | = Transformer Harmonic De-rating Factor = sqrt(2)/CF, % |

| Slip % | = SRSS sum of slip and harmonic "levels" divided by RMS level of RMS DEMOD spectra between 0 and 65 Hz. |
| --- | --- |
| Upper sb | = dB level of upper slip sideband of power line peak |
| Lower sb | = dB level of lower slip sideband of power line peak |
| Se, fund | = Location of pole pass frequency fundamental, Hz |
| Se, harm | = Number of pole pass frequency harmonics |
| Rotor bar health | = Estimate of the percent of broken or cracked rotor bars |
| RB Hlt Index | = Rotor bar health index |

| THDF | = Voltage De-rating Factor = 100 - (voltage unbalance, %)^2, % |
| --- | --- |
| Level | = Sum of spectral amplitudes of pole pass frequency fundamentals and harmonics |
| Thd | = Total harmonic distortion |
| +Ve | = Positive sequence harmonic |
| -Ve | = Negative sequence harmonic |
| Zero | = Zero sequence harmonic |

Detailed Calculations

Running Speed	= 47.119 Hz [2827 RPM]

Pole pass frequency	= 5.829 Hz [350 RPM]

Load	= 71.3 %

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Current 1 | 77.100 | 112.330 | 1.457 |
| Current 2 | 76.200 | 111.020 | 1.457 |
| Current 3 | 77.400 | 112.760 | 1.457 |
| Average | 76.900 | 112.040 | 1.457 |
| % dev | 0.9 | 0.9 | 0.0 |

THDF = 97.1

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Voltage 1 | 6258.000 | 9051.000 | 1.446 |
| Voltage 2 | 6240.000 | 9025.000 | 1.446 |
| Voltage 3 | 6264.000 | 9059.700 | 1.446 |
| Average | 6254.000 | 9045.200 | 1.446 |
| % dev | 0.2 | 0.2 | 0.0 |

VDF = 99.9

* Note-

Phase 2 and 3 CF and peak entries are assumed to be the same as phase-1.

|  |  |  | App. Power | Real Power | Reac. Power |
| --- | --- | --- | --- | --- | --- |
|  | Power factor | Impedance | kVA | kW | kVARS |
| Phase 1 | 0.545 | 81.167 | 482.030 | 262.800 | 404.090 |
| Phase 2 | 0.000 | 81.890 | 0.000 | 0.000 | 0.000 |
| Phase 3 | 0.995 | 80.930 | 482.980 | 480.600 | 47.848 |
| Avg/Total | 1.540 | 81.329 | 965.010 | 743.400 | 451.940 |
| % dev | 0.0 | 0.7 |  |  |  |

Demand Pwr = 996.51 HP

Load:71.3 %

Motor Eff.:95.7 %

Loss due to THD:

Output Pow.:699.44 KW

Output Trq.:1741.10 Ft.Lb

| Summary of Rotor Bar Health |  |  |  |  | Power line dB diff. |  | RB Hlt Index |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Se, fund |  | Se, harm | Level % | Upper SB | Lower SB |  |
| Measured | 5.829 |  | 1 | - | -62.971 | -62.704 | 0.061 |
| Severity level |  | Rotor Condition Assessment |  |  | #### Recommended Corrective Action |  |  |
| 1 |  | Excellent |  |  | None |  |  |

| Bearing condition |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Location | Bearing No. | IR | OR | T/C | BS |
| Drive end | SKF NU1022 | OK | OK | OK | OK |
| Opposite end | SKF NU1022 | OK | OK | OK | OK |

| Harmonic Distortion Results: Voltage input, from 50.018 Hz harmonics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | THD Odd % | THD Even % | +ve% | -ve % | Zero % | THD All % |
| #### Current 1 | 1.880 | 0.209 | 0.294 | 1.859 | 0.186 | 1.891 |
| Current 2 | *** | *** | *** | *** | *** | *** |
| Current 3 | *** | *** | *** | *** | *** | *** |
| Voltage 1 | 0.885 | 2.901 | 0.901 | 2.796 | 0.756 | 3.033 |
| Voltage 2 | *** | *** | *** | *** | *** | *** |
| Voltage 3 | *** | *** | *** | *** | *** | *** |

| Harmonic distortion table – Peak values, voltage is phase to ground |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Hz | Cur1 | Vlt1 | Cur2 | Vlt2 | Cur3 | Vlt3 |
| 50 | 108.0 | 8842 | *** | *** | *** | *** |
| 100 | 0.2 | 236 | *** | *** | *** | *** |
| 150 | 0.2 | 6 | *** | *** | *** | *** |
| 200 | 0.1 | 75 | *** | *** | *** | *** |
| 250 | 2.1 | 78 | *** | *** | *** | *** |
| 300 | 0.0 | 47 | *** | *** | *** | *** |
| 350 | 0.3 | 3 | *** | *** | *** | *** |
| 400 | 0.0 | 60 | *** | *** | *** | *** |
| 450 | 0.0 | 6 | *** | *** | *** | *** |
| 500 | 0.0 | 1 | *** | *** | *** | *** |
| 550 | 0.1 | 5 | *** | *** | *** | *** |
| 600 | 0.0 | 39 | *** | *** | *** | *** |

Figure 1: Current harmonic distortion plot

Figure 2: Voltage harmonic distortion plot

Figure 3: Raw Current

Figure 4: Raw Current Frequency spectrum

Figure 5: Raw Voltage

Figure 6: Raw Voltage Frequency spectrum

Figure 7: Demodulated current trace

Figure 8: Raw current spectrum

Figure 9: Demodulated current spectrum