ALL TEST 6.31 Analysis Results

#### Performance Summary

# Bottom Line

X	This induction motor is operating normally, no action is required.

This induction motor  exhibits suspicious operation, trending of the induction motor  is warranted.

This induction motor  exhibits abnormal indications, action is warranted, NOW.

# Power Factor Commentary

X	Power factor exceeds 0.85.

Power factor is below 0.85, see detailed report.

# Current Commentary

X	Current variation is within normal limits.

Current variation is beyond normal limits, see detailed report.

# Voltage Commentary

X	Voltage variation is within normal limits.

Voltage variation is beyond normal limits, see detailed report.

RMS voltage differs from nameplate by more than 5%.

# Load Commentary

X	Load on the induction motor  is consistent with nameplate values.

Load on the induction motor  exceeds nameplate values, see detailed report.

Load on the induction motor  is less than 25%.

# Phase Connection Commentary

X	Connections are normal.

Voltage ground reference is NOT neutral.

Loose connection.

# Rotor Commentary

X	Rotor bar health is normal.

Rotor bar health is questionable, see detailed report.

Load is insufficient to determine rotor bar health, at this time.

# Stator Commentary

X	Stator health is normal.

Stator mechanical health is questionable. .

Turn to turn short.

# Rotor/Stator Air-gap Characteristics

X	Dynamic or static eccentricity indications do not exist.

Indications of static eccentricity exist .

Indications of dynamic eccentricity exist.

# Harmonic Distortion Commentary

X	There is no evidence of harmonic distortion.

There is evidence of harmonic distortion, see detailed report.

# Misalignment Indications

X	There are no indications of mechanical problems like misalignment or  unbalance.

There are indications of mechanical problems like misalignment / unbalance.  Perform vibr. survey to identify and correct the cause.

INPUT SUMMARY

# NAMEPLATE INFORMATION

|  |  | Units |
| --- | --- | --- |
| Model Number | Y2 - 280-4 |  |
| Tested Equipment | Induction |  |
| Power | 75.0 | KW |
| RPM | 980.0 | Rpm |
| Poles | 6 |  |
| Phases: | 3 |  |
| Voltage | 380.0 | Volt |
| Full Load Current | 139.60 | Amp |
| No Load Current | -1.00 | Amp |
| Number of rotor bars | 108 |  |
| Number of stator slots | -1 |  |
| Torque | 730 | N.m |
| CT Ratio | 1.000 |  |
| Service Factor | 115 |  |
| Motor efficiency | -1.000 |  |
| Power factor | 0.870 |  |

Description:

Belum ada data rotor bar dan stator slot

| LEGENDS: |  |
| --- | --- |
| Impedance | = Complex Impedance = vi/ci |
| CF | = Crest Factor = (waveform peak)/(waveform rms) |
| VDF | = Transformer Harmonic De-rating Factor = sqrt(2)/CF, % |

| Slip % | = SRSS sum of slip and harmonic "levels" divided by RMS level of RMS DEMOD spectra between 0 and 65 Hz. |
| --- | --- |
| Upper sb | = dB level of upper slip sideband of power line peak |
| Lower sb | = dB level of lower slip sideband of power line peak |
| Se, fund | = Location of pole pass frequency fundamental, Hz |
| Se, harm | = Number of pole pass frequency harmonics |
| Rotor bar health | = Estimate of the percent of broken or cracked rotor bars |
| RB Hlt Index | = Rotor bar health index |

| THDF | = Voltage De-rating Factor = 100 - (voltage unbalance, %)^2, % |
| --- | --- |
| Level | = Sum of spectral amplitudes of pole pass frequency fundamentals and harmonics |
| Thd | = Total harmonic distortion |
| +Ve | = Positive sequence harmonic |
| -Ve | = Negative sequence harmonic |
| Zero | = Zero sequence harmonic |

Detailed Calculations

Running Speed	= 15.594 Hz [936 RPM]

Pole pass frequency	= 6.256 Hz [375 RPM]

Load	= 88.6 %

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Current 1 | 120.800 | 173.070 | 1.433 |
| Current 2 | 121.500 | 174.070 | 1.433 |
| Current 3 | 120.700 | 172.920 | 1.433 |
| Average | 121.000 | 173.350 | 1.433 |
| % dev | 0.4 | 0.4 | 0.0 |

THDF = 98.7

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Voltage 1 | 384.300 | 546.810 | 1.423 |
| Voltage 2 | 384.600 | 547.230 | 1.423 |
| Voltage 3 | 383.800 | 546.100 | 1.423 |
| Average | 384.230 | 546.710 | 1.423 |
| % dev | 0.1 | 0.1 | 0.0 |

VDF = 100.0

* Note-

Phase 2 and 3 CF and peak entries are assumed to be the same as phase-1.

|  |  |  | App. Power | Real Power | Reac. Power |
| --- | --- | --- | --- | --- | --- |
|  | Power factor | Impedance | kVA | kW | kVARS |
| Phase 1 | 0.885 | 3.181 | 26.769 | 23.700 | 12.446 |
| Phase 2 | 0.885 | 3.165 | 26.985 | 23.880 | 12.568 |
| Phase 3 | 0.884 | 3.180 | 26.759 | 23.650 | 12.519 |
| Avg/Total | 0.885 | 3.176 | 80.514 | 71.230 | 37.533 |
| % dev | 0.1 | 0.3 |  |  |  |

Demand Pwr = 71.2 KW

Load:88.6 %

Motor Eff.:93.3 %

Loss due to THD:

Output Pow.:65.62 KW

Output Trq.:669.1 N.m

| Summary of Rotor Bar Health |  |  |  |  | Power line dB diff. |  | RB Hlt Index |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Se, fund |  | Se, harm | Level % | Upper SB | Lower SB |  |
| Measured | 6.256 |  | 2 | 0.1 | -60.180 | -60.249 | 0.193 |
| Severity level |  | Rotor Condition Assessment |  |  | #### Recommended Corrective Action |  |  |
| 1 |  | Excellent |  |  | None |  |  |

| Harmonic Distortion Results: Voltage input, from 50.049 Hz harmonics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | THD Odd % | THD Even % | +ve% | -ve % | Zero % | THD All % |
| #### Current 1 | 0.568 | 0.056 | 0.045 | 0.563 | 0.081 | 0.571 |
| Current 2 | *** | *** | *** | *** | *** | *** |
| Current 3 | *** | *** | *** | *** | *** | *** |
| Voltage 1 | 0.689 | 0.099 | 0.109 | 0.679 | 0.107 | 0.696 |
| Voltage 2 | *** | *** | *** | *** | *** | *** |
| Voltage 3 | *** | *** | *** | *** | *** | *** |

| Harmonic distortion table – Peak values, voltage is phase to ground |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Hz | Cur1 | Vlt1 | Cur2 | Vlt2 | Cur3 | Vlt3 |
| 50 | 170.5 | 311 | *** | *** | *** | *** |
| 100 | 0.1 | 0 | *** | *** | *** | *** |
| 150 | 0.1 | 0 | *** | *** | *** | *** |
| 200 | 0.0 | 0 | *** | *** | *** | *** |
| 250 | 1.0 | 2 | *** | *** | *** | *** |
| 300 | 0.0 | 0 | *** | *** | *** | *** |
| 350 | 0.0 | 0 | *** | *** | *** | *** |
| 400 | 0.0 | 0 | *** | *** | *** | *** |
| 450 | 0.1 | 0 | *** | *** | *** | *** |
| 500 | 0.0 | 0 | *** | *** | *** | *** |
| 550 | 0.1 | 0 | *** | *** | *** | *** |
| 600 | 0.0 | 0 | *** | *** | *** | *** |

Figure 1: Current harmonic distortion plot

Figure 2: Voltage harmonic distortion plot

Figure 3: Raw Current

Figure 4: Raw Current Frequency spectrum

Figure 5: Raw Voltage

Figure 6: Raw Voltage Frequency spectrum

Figure 7: Demodulated current trace

Figure 8: Raw current spectrum

Figure 9: Demodulated current spectrum