ALL TEST 6.31 Analysis Results

#### Performance Summary

# Bottom Line

This induction motor is operating normally, no action is required.

X	This induction motor  exhibits suspicious operation, trending of the induction motor  is warranted.

This induction motor  exhibits abnormal indications, action is warranted, NOW.

# Power Factor Commentary

X	Power factor exceeds 0.85.

Power factor is below 0.85, see detailed report.

# Current Commentary

X	Current variation is within normal limits.

Current variation is beyond normal limits, see detailed report.

# Voltage Commentary

X	Voltage variation is within normal limits.

Voltage variation is beyond normal limits, see detailed report.

RMS voltage differs from nameplate by more than 5%.

# Load Commentary

X	Load on the induction motor  is consistent with nameplate values.

Load on the induction motor  exceeds nameplate values, see detailed report.

Load on the induction motor  is less than 25%.

# Phase Connection Commentary

X	Connections are normal.

Voltage ground reference is NOT neutral.

Loose connection.

# Rotor Commentary

Rotor bar health is normal.

X	Rotor bar health is questionable, see detailed report.

Load is insufficient to determine rotor bar health, at this time.

# Stator Commentary

X	Stator health is normal.

Stator mechanical health is questionable. .

Turn to turn short.

# Rotor/Stator Air-gap Characteristics

X	Dynamic or static eccentricity indications do not exist.

Indications of static eccentricity exist .

Indications of dynamic eccentricity exist.

# Harmonic Distortion Commentary

X	There is no evidence of harmonic distortion.

There is evidence of harmonic distortion, see detailed report.

INPUT SUMMARY

# NAMEPLATE INFORMATION

|  |  | Units |
| --- | --- | --- |
| Manufacturer | SHANDONG SHUANG |  |
| Model Number | HN2-225 |  |
| Tested Equipment | Induction |  |
| Power | 45.0 | KW |
| RPM | 2970.0 | Rpm |
| Poles | 2 |  |
| Phases: | 3 |  |
| Voltage | 380.0 | Volt |
| Full Load Current | 78.00 | Amp |
| No Load Current | -1.00 | Amp |
| Number of rotor bars | 30 |  |
| Number of stator slots | 24 |  |
| Torque | 145 | N.m |
| CT Ratio | 1.000 |  |
| Service Factor | 115 |  |
| Motor efficiency | -1.000 |  |
| Power factor | -1.000 |  |

Description:

Belum ada data rotor bar dan stator slot

| LEGENDS: |  |
| --- | --- |
| Impedance | = Complex Impedance = vi/ci |
| CF | = Crest Factor = (waveform peak)/(waveform rms) |
| VDF | = Transformer Harmonic De-rating Factor = sqrt(2)/CF, % |

| Slip % | = SRSS sum of slip and harmonic "levels" divided by RMS level of RMS DEMOD spectra between 0 and 65 Hz. |
| --- | --- |
| Upper sb | = dB level of upper slip sideband of power line peak |
| Lower sb | = dB level of lower slip sideband of power line peak |
| Se, fund | = Location of pole pass frequency fundamental, Hz |
| Se, harm | = Number of pole pass frequency harmonics |
| Rotor bar health | = Estimate of the percent of broken or cracked rotor bars |
| RB Hlt Index | = Rotor bar health index |

| THDF | = Voltage De-rating Factor = 100 - (voltage unbalance, %)^2, % |
| --- | --- |
| Level | = Sum of spectral amplitudes of pole pass frequency fundamentals and harmonics |
| Thd | = Total harmonic distortion |
| +Ve | = Positive sequence harmonic |
| -Ve | = Negative sequence harmonic |
| Zero | = Zero sequence harmonic |

Detailed Calculations

Running Speed	= 49.622 Hz [2977 RPM]

Pole pass frequency	= 0.854 Hz [51 RPM]

Load	= 74.4 %

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Current 1 | 60.670 | 87.502 | 1.442 |
| Current 2 | 62.740 | 90.488 | 1.442 |
| Current 3 | 62.630 | 90.329 | 1.442 |
| Average | 62.013 | 89.440 | 1.442 |
| % dev | 2.2 | 2.2 | 0.0 |

THDF = 98.1

| Time |  |  |  |
| --- | --- | --- | --- |
|  | RMS | Peak | CF |
| Voltage 1 | 389.000 | 546.290 | 1.404 |
| Voltage 2 | 390.700 | 548.680 | 1.404 |
| Voltage 3 | 390.500 | 548.400 | 1.404 |
| Average | 390.070 | 547.790 | 1.404 |
| % dev | 0.3 | 0.3 | 0.0 |

VDF = 99.9

* Note-

Phase 2 and 3 CF and peak entries are assumed to be the same as phase-1.

|  |  |  | App. Power | Real Power | Reac. Power |
| --- | --- | --- | --- | --- | --- |
|  | Power factor | Impedance | kVA | kW | kVARS |
| Phase 1 | 0.876 | 6.412 | 13.657 | 11.957 | 6.598 |
| Phase 2 | 0.885 | 6.227 | 14.098 | 12.482 | 6.553 |
| Phase 3 | 0.862 | 6.235 | 14.136 | 12.189 | 7.158 |
| Avg/Total | 0.874 | 6.291 | 41.890 | 36.628 | 20.310 |
| % dev | 1.4 | 1.9 |  |  |  |

Demand Pwr = 36.6 KW

Load:74.4 %

Motor Eff.:91.3 %

Loss due to THD:

Output Pow.:32.47 KW

Output Trq.:104.1 N.m

| Summary of Rotor Bar Health |  |  |  |  | Power line dB diff. |  | RB Hlt Index |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Se, fund |  | Se, harm | Level % | Upper SB | Lower SB |  |
| Measured | 0.854 |  | 2 | 0.4 | -46.679 | -47.357 | 0.370 |
| Severity level |  | Rotor Condition Assessment |  |  | #### Recommended Corrective Action |  |  |
| 4 |  | Rotor bar crack may be developing or problems with high resistance joints |  |  | Reduce survey intervals, trend closely |  |  |

| Harmonic Distortion Results: Voltage input, from 50.049 Hz harmonics |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | THD Odd % | THD Even % | +ve% | -ve % | Zero % | THD All % |
| #### Current 1 | 2.095 | 0.386 | 0.560 | 1.959 | 0.624 | 2.131 |
| Current 2 | *** | *** | *** | *** | *** | *** |
| Current 3 | *** | *** | *** | *** | *** | *** |
| Voltage 1 | 1.454 | 0.115 | 0.487 | 1.342 | 0.298 | 1.459 |
| Voltage 2 | *** | *** | *** | *** | *** | *** |
| Voltage 3 | *** | *** | *** | *** | *** | *** |

| Harmonic distortion table – Peak values, voltage is phase to ground |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Hz | Cur1 | Vlt1 | Cur2 | Vlt2 | Cur3 | Vlt3 |
| 50 | 84.4 | 320 | *** | *** | *** | *** |
| 100 | 0.3 | 0 | *** | *** | *** | *** |
| 150 | 0.5 | 1 | *** | *** | *** | *** |
| 200 | 0.1 | 0 | *** | *** | *** | *** |
| 250 | 1.7 | 4 | *** | *** | *** | *** |
| 300 | 0.0 | 0 | *** | *** | *** | *** |
| 350 | 0.4 | 1 | *** | *** | *** | *** |
| 400 | 0.0 | 0 | *** | *** | *** | *** |
| 450 | 0.1 | 1 | *** | *** | *** | *** |
| 500 | 0.0 | 0 | *** | *** | *** | *** |
| 550 | 0.1 | 0 | *** | *** | *** | *** |
| 600 | 0.0 | 0 | *** | *** | *** | *** |

Figure 1: Current harmonic distortion plot

Figure 2: Voltage harmonic distortion plot

Figure 3: Raw Current

Figure 4: Raw Current Frequency spectrum

Figure 5: Raw Voltage

Figure 6: Raw Voltage Frequency spectrum

Figure 7: Demodulated current trace

Figure 8: Raw current spectrum

Figure 9: Demodulated current spectrum