## RESUME
| PT PLN INDONESIA POWER | [7 empty] | No. Dok | : FORM.JRG.F.05.001
| UBP JERANJANG | [7 empty] | Tgl Terbit | : 1 Sep 2016
| BIDANG RCBM | [7 empty] | Rev | : 00
| LAPORAN PDM | [7 empty] | Hal | :
LAPORAN IR THERMOGRAPHY BULAN JULI 2026 UNIT BISNIS PEMBANGKITAN JERANJANG
UNIT | STATUS IR THERMOGRAPHY
| NORMAL | LOW | MEDIUM | HIGH | CRITICAL | STANDBY |  | Keterangan :
UNIT 1 | 10 | 7 | 4 | 0 | 0 | 4 |  | NORMAL | = Kondisi baik
UNIT 2 | 11 | 4 | 1 | 0 | 0 | 3 |  | LOW | = Periksa saat pemeliharaan
UNIT 3 | 18 | 4 | 4 | 0 | 0 | 7 |  | MEDIUM | = Rencana pebaikan (Max. 30 hari)
COAL HANDLING | 10 | 0 | 2 | 0 | 0 | 6 |  | HIGH | = Perbaikan segera
TOTAL | 49 | 15 | 11 | 0 | 0 | 20 | 95 | CRITICAL | = Kondisi darurat
PERSENTASE (%) | 51.5789 | 15.7895 | 11.5789 | 0 | 0 | 21.0526 | 100 | STANDBY | = Peralatan standby

## SUMMARY
Unit | No KKS | Description | Standard | Status Kondisi Terakhir
1 | LJ10PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 1A | FLIR | Low | Normal (FLIR) | 61 | 55.96%
1 | LJ10PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 1B | FLIR | Normal | Low (FLIR) | 15 | 13.76%
1 | LJ10LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 1A | FLIR | STD BY | Medium (FLIR) | 12 | 11.01%
1 | LJ10LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 1B | FLIR | Medium | High (FLIR) | 0 | 0%
1 | LJ10HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 1A | FLIR | Normal | Critical (FLIR) | 0 | 0%
1 | LJ10HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 1B | FLIR | Low | Standby | 21 | 19.27%
1 | LJ10HLB10AN001-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 1A | FLIR | Low | Unit 1 | 109
1 | LJ10HLB10AN002-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 1B | FLIR | Low | Normal (FLIR) | 14
1 | LJ10HLB10AN003-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 1A | FLIR | Normal | Low (FLIR) | 7
1 | LJ10HLB10AN004-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 1B | FLIR | Low | Medium (FLIR) | 5
1 | LJ10LCB10AP010-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 1A | FLIR | STD BY | High (FLIR) | 0
1 | LJ10LCB10AP020-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 1B | FLIR | Low | Critical (FLIR) | 0
1 | LJ10PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 1A | FLIR | Medium | Standby | 4
1 | LJ10PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 1B | FLIR | Medium | Unit 2
1 | LJ10MAG10AP011-001 | EQUIPMENT-VACUUM PUMP 1A | FLIR | Medium | Normal (FLIR) | 14
1 | LJ10MAG10AP012-001 | EQUIPMENT-VACUUM PUMP 1B | FLIR | Low | Low (FLIR) | 4
1 | LJ10GCK10AP005-001 | EQUIPMENT-BWRO PUMP 1A | FLIR | Normal | Medium (FLIR) | 1
1 | LJ10GCK10AP006-001 | EQUIPMENT-BWRO PUMP 1B | FLIR | STD BY | High (FLIR) | 0
1 | LJ10GCK10AP007-001 | EQUIPMENT-HIGH PRESSURE SWRO PUMP 1A | FLIR | STD BY | Critical (FLIR) | 0
1 | LJ10GCK10AP008-001 | EQUIPMENT-HIGH PRESSURE SWRO PUMP 1B | FLIR | Normal | Standby | 5
1 | LJ10MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 1 | FLIR | Normal | Unit 3
1 | LJ10MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 1 | FLIR | Normal | Normal (FLIR) | 17
1 | LJ10BFT10GT001-001 | EQUIPMENT-LV TRANSFORMER 43T UNIT 1 | FLIR | Normal | Low (FLIR) | 4
1 | LJ10BFT10GT002-001 | EQUIPMENT-LV TRANSFORMER 44T UNIT 1 | FLIR | Normal | Medium (FLIR) | 5
1 | LJ10BFT10GT007-001 | EQUIPMENT- LV TRANSFORMER EXCITATION | FLIR | Normal | High (FLIR) | 0
1 | LJ10MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 1 | FLIR | Medium | Critical (FLIR) | 0
1 | LJ10MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 1 | FLIR | Normal | Standby | 11
1 | LJ10BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 34.5 MVA 150/6.3 KV UNIT 1 | FLIR | Normal | Common
1 | LJ10BBT10GT002-001 | EQUIPMENT-TRANSFORMER ASH HANDLING 1 | FLIR | Normal | Normal (FLIR) | 16
1 | LJ10BBT10GT003-001 | EQUIPMENT-TRANSFORMER ASH HANDLING 2 | FLIR | Normal | Low (FLIR) | 0
2 | LJ20PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 2A | FLIR | STD BY | Medium (FLIR) | 1
2 | LJ20PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 2B | FLIR | Normal | High (FLIR) | 0
2 | LJ20LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 2A | FLIR | STD BY | Critical (FLIR) | 0
2 | LJ20LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 2B | FLIR | Low | Standby | 1
2 | LJ20HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 2A | FLIR | Normal
2 | LJ20HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 2B | FLIR | Normal
2 | LJ20HLB10AN001-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 2A | FLIR | Low
2 | LJ20HLB10AN002-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 2B | FLIR | Low
2 | LJ20HLB10AN003-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 2A | FLIR | Low
2 | LJ20HLB10AN004-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 2B | FLIR | Normal
2 | LJ20LCB10AP010-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 2A | FLIR | STD BY
2 | LJ20LCB10AP020-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 2B | FLIR | Normal
2 | LJ20PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 2A | FLIR | Normal
2 | LJ20PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 2B | FLIR | Normal
2 | LJ20MAG10AP011-001 | EQUIPMENT-VACUUM PUMP 2A | FLIR | Normal
2 | LJ20MAG10AP012-001 | EQUIPMENT-VACUUM PUMP 2B | FLIR | Medium
2 | LJ20MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 2 | FLIR | Normal
2 | LJ20MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 2 | FLIR | Normal
2 | LJ20BFT10GT001-001 | EQUIPMENT-LV TRANSFORMER 43T UNIT 2 | FLIR | Normal
2 | LJ20BFT10GT002-001 | EQUIPMENT-LV TRANSFORMER 44T UNIT 2 | FLIR | Normal
2 | LJ20BFT10GT007-001 | EQUIPMENT- LV TRANSFORMER EXCITATION | FLIR | Normal
2 | LJ20MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 2 | FLIR | STD BY
2 | LJ20MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 2 | FLIR | STD BY
2 | LJ20BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 34.5 MVA 150/6.3 KV UNIT 2 | FLIR | Normal
3 | LJ30LCB10AP001-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3A | FLIR | Low
3 | LJ30LCB10AP002-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3B | FLIR | Normal
3 | LJ30LCB10AP003-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3C | FLIR | Normal
3 | LJ30MAG10AP011-001 | EQUIPMENT-WATER JET PUMP (WJP) 3A | FLIR | Normal
3 | LJ30MAG10AP012-001 | EQUIPMENT-WATER JET PUMP (WJP) 3B | FLIR | STD BY
3 | LJ30LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 3A | FLIR | Medium
3 | LJ30LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 3B | FLIR | STD BY
3 | LJ30PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 3A | FLIR | Normal
3 | LJ30PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 3B | FLIR | Medium
3 | LJ30PGB10AN001-001 | EQUIPMENT-COOLING TOWER FAN 3A | FLIR | Normal
3 | LJ30PGB10AN002-001 | EQUIPMENT-COOLING TOWER FAN 3B | FLIR | Low
3 | LJ30HLB20AN010-001 | EQUIPMENT-SECONDARY AIR FAN UNIT 3 | FLIR | Normal
3 | LJ30HLB10AN010-001 | EQUIPMENT-PRIMARY AIR FAN UNIT 3 | FLIR | Normal
3 | LJ30HFC10AN011-001 | EQUIPMENT-RECIRCULATING AIR FAN (RAF) 3A | FLIR | STD BY
3 | LJ30HFC10AN012-001 | EQUIPMENT-RECIRCULATING AIR FAN (RAF) 3B | FLIR | Normal
3 | LJ30HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 3A | FLIR | Low
3 | LJ30HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 3B | FLIR | Low
3 | LJ30PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 3A | FLIR | STD BY
3 | LJ30PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 3B | FLIR | Normal
3 | LJ30GCF10AP007-001 | EQUIPMENT-HIGH PRESURE BWRO PUMP 3A | FLIR | Normal
3 | LJ30GCF10AP008-001 | EQUIPMENT-HIGH PRESURE BWRO PUMP 3B | FLIR | -
3 | LJ30GCF10AP001-001 | EQUIPMENT-HIGH PRESURE SWRO PUMP 3A | FLIR | Normal
3 | LJ30GCF10AP002-001 | EQUIPMENT-HIGH PRESURE SWRO PUMP 3B | FLIR | STD BY
3 | LJ30MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 3 | FLIR | Medium
3 | LJ30MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 3 | FLIR | Medium
3 | LJ30BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 40 MVA 150/6.3 KV UNIT 3 | FLIR | Normal
3 | LJ30BBT10GT001-001 | EQUIPMENT-UNIT AUXILIARY TRANSFORMER (UAT) 6.3 MVA UNIT 3 | FLIR | Normal
3 | LJ00SGA10AP002-001 | EQUIPMENT-JOCKEY PUMP 3A | FLIR | Normal
3 | LJ00SGA10AP003-001 | EQUIPMENT-JOCKEY PUMP 3B | FLIR | STD BY
3 | LJ00SGA10AP001-001 | EQUIPMENT-FIRE FIGHTING PUMP WITH MOTOR UNIT 3 | FLIR | Medium
3 | LJ00SGA10AP004-001 | EQUIPMENT-FIRE FIGHTING PUMP WITH DIESEL MOTOR UNIT 3 | FLIR | Normal
3 | LJ30BFA10GT003-001 | EQUIPMENT-LV TRANSFORMER HSB | FLIR | Normal
3 | LJ30BFA10GT002-001 | EQUIPMENT-LV TRANSFORMER 40.B | FLIR | Normal
3 | LJ30BFA10GT001-001 | EQUIPMENT-LV TRANSFORMER 41.B | FLIR | STD BY
3 | LJ30MAV10AP004-001 | EQUIPMENT-JACKING OIL PUMP 1 UNIT 3 | FLIR | STD BY
3 | LJ30MAV10AP005-001 | EQUIPMENT-JACKING OIL PUMP 2 UNIT 3 | FLIR | STD BY
3 | LJ30MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 3 | FLIR | STD BY
3 | LJ30MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 3 | FLIR | STD BY
0 | LJ00EBA40AF001-001 | EQUIPMENT-BELT CONVEYOR 4.1 | FLIR | Normal
0 | LJ00EBA40AF002-001 | EQUIPMENT-BELT CONVEYOR 4.2 | FLIR | Normal
0 | LJ00EBA50AF001-001 | EQUIPMENT-BELT CONVEYOR 5.1 | FLIR | Normal
0 | LJ00EBA50AF002-001 | EQUIPMENT-BELT CONVEYOR 5.2 | FLIR | Normal
0 | LJ00EBA60AF001-001 | EQUIPMENT-BELT CONVEYOR 7.1 | FLIR | Normal
0 | LJ00EBA60AF002-001 | EQUIPMENT-BELT CONVEYOR 7.2 | FLIR | Normal
0 | LJ00EBA70AF001-001 | EQUIPMENT-BELT CONVEYOR 8.1 | FLIR | Normal
0 | LJ00EBA70AF002-001 | EQUIPMENT-BELT CONVEYOR 8.2 | FLIR | Medium
0 | LJ00EBA80AF001-001 | EQUIPMENT-BELT CONVEYOR 10.1 | FLIR | Normal
0 | LJ00EBA80AF002-001 | EQUIPMENT-BELT CONVEYOR 10.2 | FLIR | Normal
0 | LJ00EBC10AT003-001 | EQUIPMENT-CRUSHER 1 | FLIR | Normal
0 | LJ00EBC10AT004-001 | EQUIPMENT-CRUSHER 2 | FLIR | Normal
0 | LJ00EBC10AT001-001 | EQUIPMENT-ROLLING SCREEN 1 | FLIR | Normal
0 | LJ00EBC10AT002-001 | EQUIPMENT-ROLLING SCREEN 2 | FLIR | Normal
0 | LJ00EBA40AT001-001 | EQUIPMENT-VIBRATING FEEDER 1 | FLIR | Normal
0 | LJ00EBA40AT002-001 | EQUIPMENT-VIBRATING FEEDER 2 | FLIR | Normal
0 | LJ00BBA10GT001-001 | EQUIPMENT-TRANSFORMER COAL HANDLING 1 | FLIR | STD BY
0 | LJ00BBA10GT002-001 | EQUIPMENT-TRANSFORMER COAL HANDLING 2 | FLIR | Normal

## REKOMENDASI
EXECUTIVE SUMMARY IR THERMOGRAPHY JULI 2026
Unit | No. KKS | Description | Measurement Point | Upper Warning Limit Maximo | Upper Action Limit Maximo | Analysis Standard | Status per Point Measurement | Overall Status Equipment | T rise | T max Reference | Data Analysis |  | Keterangan
[11 empty] | Date | ( °C )
1 | LJ10PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 1A | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-14 | 56 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-14 | 44.7
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-14 | 46.1
|  |  | Bearing 3 pump | 61 | 71 | FLIR | Low |  | 5.4 | 50 | 2026-07-14 | 55.4
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 2.5 | 30 | 2026-07-14 | 32.5
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 2.2 | 30 | 2026-07-14 | 32.2
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 2.2 | 30 | 2026-07-14 | 32.2
1 | LJ10PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 1B | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-23 | 52.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 47.6
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 49.3
|  |  | Bearing 3 pump | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 50
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 3.6 | 30 | 2026-07-23 | 33.6
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 3.5 | 30 | 2026-07-23 | 33.5
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 3.3 | 30 | 2026-07-23 | 33.3
1 | LJ10LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 1A | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 2 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 3 Fluid Coupling | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 4 Fluid Coupling | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 5 pump | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 6 pump | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Conection Phasa R | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa S | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa T | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
1 | LJ10LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 1B | Cover winding motor | 71 | 81 | FLIR | Low | Medium | 8.7 | 60 | 2026-07-20 | 68.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | Normal |  | 3.5 | 55 | 2026-07-20 | 58.5
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0.3 | 50 | 2026-07-20 | 50.3
|  |  | Bearing 3 Fluid Coupling | 61 | 71 | FLIR | Normal |  | 1.1 | 50 | 2026-07-20 | 51.1
|  |  | Bearing 4 Fluid Coupling | 61 | 71 | FLIR | Normal |  | 0.1 | 50 | 2026-07-20 | 50.1
|  |  | Bearing 5 pump | 61 | 71 | FLIR | Normal |  | 0.6 | 50 | 2026-07-20 | 50.6
|  |  | Bearing 6 pump | 61 | 71 | FLIR | Medium |  | 17.1 | 50 | 2026-07-20 | 67.1
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0.9 | 30 | 2026-07-20 | 30.9
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0.9 | 30 | 2026-07-20 | 30.9
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0.9 | 30 | 2026-07-20 | 30.9
1 | LJ10HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 1A | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0.9 | 60 | 2026-07-13 | 60.9 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-13 | 35.5
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 2.7 | 50 | 2026-07-13 | 52.7
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-13 | 48.8
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-13 | 48.8
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 27.7
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 27.7
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 27.8
1 | LJ10HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 1B | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-27 | 57.8 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 38.1
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Low |  | 7.7 | 50 | 2026-07-27 | 57.7
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 46.1
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 47.3
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 2.4 | 30 | 2026-07-27 | 32.4
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 3.4 | 30 | 2026-07-27 | 33.4
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 2.9 | 30 | 2026-07-27 | 32.9
1 | LJ10HLB10AN001-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 1A | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-13 | 51.9 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-13 | 34.9
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 3.7 | 50 | 2026-07-13 | 53.7
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Low |  | 8.4 | 50 | 2026-07-13 | 58.4
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Low |  | 10.3 | 50 | 2026-07-13 | 60.3
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 22.2
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 22.3
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 22.3
1 | LJ10HLB10AN002-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 1B | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-27 | 48.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-27 | 37.2
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 45.8
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Low |  | 5.3 | 50 | 2026-07-27 | 55.3
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Low |  | 6.7 | 50 | 2026-07-27 | 56.7
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0.8 | 30 | 2026-07-27 | 30.8
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0.8 | 30 | 2026-07-27 | 30.8
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0.7 | 30 | 2026-07-27 | 30.7
1 | LJ10HLB10AN003-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 1A | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-13 | 51.2 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-13 | 33.4
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-13 | 48.1
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-13 | 48.9
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-13 | 49
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-13 | 0
1 | LJ10HLB10AN004-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 1B | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-27 | 58.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 41
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Low |  | 8.1 | 50 | 2026-07-27 | 58.1
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 3.4 | 50 | 2026-07-27 | 53.4
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Low |  | 5.4 | 50 | 2026-07-27 | 55.4
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 3.1 | 30 | 2026-07-27 | 33.1
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 3.2 | 30 | 2026-07-27 | 33.2
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 3 | 30 | 2026-07-27 | 33
1 | LJ10LCB10AP010-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 1A | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 3 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Conection Phasa R | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
|  |  | Conection Phasa S | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
|  |  | Conection Phasa T | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
1 | LJ10LCB10AP020-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 1B | Cover winding motor | 71 | 81 | FLIR | Low | Low | 6.1 | 60 | 2026-07-06 | 66.1 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-06 | 40.8
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 2.2 | 60 | 2026-07-06 | 62.2
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-06 | 59.2
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-06 | 38.4
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0.6 | 40 | 2026-07-06 | 40.6
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-06 | 37.9
1 | LJ10PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 1A | Cover winding motor | 81 | 91 | FLIR | Normal | Medium | 0 | 70 | 2026-07-14 | 65.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 2.8 | 50 | 2026-07-14 | 52.8
|  |  | Bearing 2 motor | 76 | 86 | FLIR | Normal |  | 1.5 | 65 | 2026-07-14 | 66.5
|  |  | Bearing 3 pump | 51 | 61 | FLIR | Normal |  | 3.6 | 40 | 2026-07-14 | 43.6
|  |  | Conection Phasa R | 51 | 61 | FLIR | Low |  | 5 | 40 | 2026-07-14 | 45
|  |  | Conection Phasa S | 51 | 61 | FLIR | Low |  | 8.3 | 40 | 2026-07-14 | 48.3
|  |  | Conection Phasa T | 51 | 61 | FLIR | Medium |  | 19.5 | 40 | 2026-07-14 | 59.5
1 | LJ10PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 1B | Cover winding motor | 81 | 91 | FLIR | Low | Medium | 7.6 | 70 | 2026-07-06 | 77.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0.5 | 50 | 2026-07-06 | 50.5
|  |  | Bearing 2 motor | 76 | 86 | FLIR | Normal |  | 0 | 65 | 2026-07-06 | 57.1
|  |  | Bearing 3 pump | 51 | 61 | FLIR | Medium |  | 15.8 | 40 | 2026-07-06 | 55.8
|  |  | Conection Phasa R | 51 | 61 | FLIR | Low |  | 5 | 40 | 2026-07-06 | 45
|  |  | Conection Phasa S | 51 | 61 | FLIR | Low |  | 9.1 | 40 | 2026-07-06 | 49.1
|  |  | Conection Phasa T | 51 | 61 | FLIR | Medium |  | 16.3 | 40 | 2026-07-06 | 56.3
1 | LJ10MAG10AP011-001 | EQUIPMENT-VACUUM PUMP 1A | Cover winding motor | 71 | 81 | FLIR | Normal | Medium | 1.2 | 60 | 2026-07-27 | 61.2 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0.4 | 50 | 2026-07-27 | 50.4
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 1.4 | 60 | 2026-07-27 | 61.4
|  |  | Bearing 3 pump | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 46
|  |  | Bearing 4 pump | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 49.1
|  |  | Conection Phasa R | 51 | 61 | FLIR | Medium |  | 11.5 | 40 | 2026-07-27 | 51.5
|  |  | Conection Phasa S | 51 | 61 | FLIR | Low |  | 7.2 | 40 | 2026-07-27 | 47.2
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 1.4 | 40 | 2026-07-27 | 41.4
1 | LJ10MAG10AP012-001 | EQUIPMENT-VACUUM PUMP 1B | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0.7 | 60 | 2026-07-27 | 60.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 4.7 | 50 | 2026-07-27 | 54.7
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0.7 | 60 | 2026-07-27 | 60.7
|  |  | Bearing 3 pump | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 47.9
|  |  | Bearing 4 pump | 61 | 71 | FLIR | Low |  | 9.1 | 50 | 2026-07-27 | 59.1
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 3.7 | 40 | 2026-07-27 | 43.7
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0.5 | 40 | 2026-07-27 | 40.5
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-27 | 39.2
1 | LJ10GCK10AP005-001 | EQUIPMENT-BWRO PUMP 1A | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 1.7 | 50 | 2026-07-28 | 51.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-28 | 40.8
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-28 | 48.3
1 | LJ10GCK10AP006-001 | EQUIPMENT-BWRO PUMP 1B | Cover winding motor | 61 | 71 | FLIR | STD BY | STD BY | STD BY | 50 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
1 | LJ10GCK10AP007-001 | EQUIPMENT-HIGH PRESSURE SWRO PUMP 1A | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
1 | LJ10GCK10AP008-001 | EQUIPMENT-HIGH PRESSURE SWRO PUMP 1B | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-27 | 49.4 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 41.9
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-27 | 46.2
1 | LJ10MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 1 | Bearing 1 | 101 | 111 | FLIR | Normal | Normal | 0 | 90 | 2026-07-14 | 68 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 2 | 76 | 86 | FLIR | Normal |  | 3.1 | 65 | 2026-07-14 | 68.1
1 | LJ10MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 1 | Cover winding motor | 81 | 91 | FLIR | Normal | Normal | 0 | 70 | 2026-07-14 | 63.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 3 | 71 | 81 | FLIR | Normal |  | 0.8 | 60 | 2026-07-14 | 60.8
|  |  | Bearing 4 | 61 | 71 | FLIR | Normal |  | 2.8 | 50 | 2026-07-14 | 52.8
1 | LJ10BFT10GT001-001 | EQUIPMENT-LV TRANSFORMER 43T UNIT 1 | Body Timur | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-30 | 42.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Barat | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-30 | 40.5
|  |  | Phasa 6,3 Kv R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 35
|  |  | Phasa 6,3 Kv S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 36.4
|  |  | Phasa 6,3 Kv T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 37.7
|  |  | Phasa 380 V R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 39
|  |  | Phasa 380 V S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 38.5
|  |  | Phasa 380 V T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 37.9
1 | LJ10BFT10GT002-001 | EQUIPMENT-LV TRANSFORMER 44T UNIT 1 | Body Timur | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-30 | 44.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Barat | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-30 | 42.9
|  |  | Phasa 6,3 Kv R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 36
|  |  | Phasa 6,3 Kv S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 37.4
|  |  | Phasa 6,3 Kv T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 36.5
|  |  | Phasa 380 V R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 34.8
|  |  | Phasa 380 V S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 36.7
|  |  | Phasa 380 V T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 37.4
1 | LJ10BFT10GT007-001 | EQUIPMENT- LV TRANSFORMER EXCITATION | Body Timur | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-28 | 29.9 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Barat | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-28 | 0
|  |  | Phasa 6,3 Kv R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-28 | 24.3
|  |  | Phasa 6,3 Kv S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-28 | 24.6
|  |  | Phasa 6,3 Kv T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-28 | 24.5
|  |  | Phasa 380 V R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-28 | 26.6
|  |  | Phasa 380 V S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-28 | 26.5
|  |  | Phasa 380 V T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-28 | 25.7
1 | LJ10MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 1 | Cover winding motor | 71 | 81 | FLIR | Low | Medium | 6.4 | 60 | 2026-07-20 | 66.4 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | Low |  | 6.4 | 45 | 2026-07-20 | 51.4
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Medium |  | 11.6 | 55 | 2026-07-20 | 66.6
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 48.8
|  |  | Bearing 4 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 36.8
1 | LJ10MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 1 | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-20 | 42.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | Normal |  | 4.1 | 45 | 2026-07-20 | 49.1
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-20 | 49.5
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 42.7
|  |  | Bearing 4 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 45.3
1 | LJ10BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 34.5 MVA 150/6.3 KV UNIT 1 | Body Transformer sisi Utara | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-20 | 57.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Transformer sisi Selatan | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 53.6
|  |  | Body Transformer sisi Barat | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 57.7
|  |  | Body Transformer sisi Timur | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 59.7
|  |  | Bushing Trafo Phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-20 | 33.7
|  |  | Bushing Trafo Phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-20 | 33.1
|  |  | Bushing Trafo Phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-20 | 33.2
|  |  | Arester Trafo phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-20 | 29.1
|  |  | Arester Trafo phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-20 | 28.9
|  |  | Arester Trafo phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-20 | 29
1 | LJ10BBT10GT002-001 | EQUIPMENT-TRANSFORMER ASH HANDLING 1 | Body Transformer sisi Utara | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-13 | 37.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Transformer sisi Selatan | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-13 | 38.4
|  |  | Body Transformer sisi Barat | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-13 | 38.5
|  |  | Body Transformer sisi Timur | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-13 | 37.2
|  |  | Bushing Primary Phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-13 | 32.2
|  |  | Bushing Primary Phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-13 | 31.4
|  |  | Bushing Primary Phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-13 | 32.1
|  |  | Secondary Phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-13 | 31.7
|  |  | Secondary Phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-13 | 31.6
|  |  | Secondary Phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-13 | 31.3
|  |  | Secondary Phasa N | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-13 | 29.7
1 | LJ10BBT10GT003-001 | EQUIPMENT-TRANSFORMER ASH HANDLING 2 | Body Transformer sisi Utara | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-27 | 30.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Transformer sisi Selatan | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-27 | 48.2
|  |  | Body Transformer sisi Barat | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-27 | 31.9
|  |  | Body Transformer sisi Timur | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-27 | 31.4
|  |  | Bushing Primary Phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-27 | 30
|  |  | Bushing Primary Phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-27 | 30.6
|  |  | Bushing Primary Phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-27 | 30.3
|  |  | Secondary Phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-27 | 30.3
|  |  | Secondary Phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-27 | 30.4
|  |  | Secondary Phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-27 | 30.3
|  |  | Secondary Phasa N | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-27 | 30.9
2 | LJ20PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 2A | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 3 pump | 81 | 91 | FLIR | STD BY |  | STD BY | 70 |  | STD BY
|  |  | Conection Phasa R | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa S | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa T | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
2 | LJ20PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 2B | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-23 | 58.1 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 46.6
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 49.4
|  |  | Bearing 3 pump | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 0
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 0
2 | LJ20LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 2A | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 2 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 3 Fluid Coupling | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 4 Fluid Coupling | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 5 pump | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 6 pump | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Conection Phasa R | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa S | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa T | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
2 | LJ20LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 2B | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-21 | 60 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-21 | 53.9
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 49.7
|  |  | Bearing 3 Fluid Coupling | 61 | 71 | FLIR | Low |  | 7.3 | 50 | 2026-07-21 | 57.3
|  |  | Bearing 4 Fluid Coupling | 61 | 71 | FLIR | Low |  | 8.9 | 50 | 2026-07-21 | 58.9
|  |  | Bearing 5 pump | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 46.5
|  |  | Bearing 6 pump | 61 | 71 | FLIR | Low |  | 7 | 50 | 2026-07-21 | 57
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
2 | LJ20HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 2A | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-21 | 50 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 36.4
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 1.1 | 50 | 2026-07-21 | 51.1
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 39.2
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 40.2
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
2 | LJ20HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 2B | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-21 | 55.4 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 38.9
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 4.9 | 50 | 2026-07-21 | 54.9
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 41.8
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 42.6
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
2 | LJ20HLB10AN001-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 2A | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-21 | 53.8 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0.3 | 40 | 2026-07-21 | 40.3
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Low |  | 5.2 | 50 | 2026-07-21 | 55.2
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 4.2 | 50 | 2026-07-21 | 54.2
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 1 | 50 | 2026-07-21 | 51
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
2 | LJ20HLB10AN002-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 2B | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-21 | 57.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 1.1 | 40 | 2026-07-21 | 41.1
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Low |  | 10.7 | 50 | 2026-07-21 | 60.7
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 3.1 | 50 | 2026-07-21 | 53.1
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Low |  | 6.7 | 50 | 2026-07-21 | 56.7
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
2 | LJ20HLB10AN003-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 2A | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-21 | 53.2 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Low |  | 6.6 | 50 | 2026-07-21 | 56.6
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 3.9 | 50 | 2026-07-21 | 53.9
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 43.5
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 47.1
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
2 | LJ20HLB10AN004-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 2B | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-21 | 52.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 3.4 | 50 | 2026-07-21 | 53.4
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 3.6 | 50 | 2026-07-21 | 53.6
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 41.1
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 45.3
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 0
2 | LJ20LCB10AP010-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 2A | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 3 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Conection Phasa R | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
|  |  | Conection Phasa S | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
|  |  | Conection Phasa T | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
2 | LJ20LCB10AP020-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 2B | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 1.8 | 60 | 2026-07-20 | 61.8 | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-20 | 40.5
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 45.8
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-20 | 53.6
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-20 | 38
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-20 | 38.1
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-20 | 38.3
2 | LJ20PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 2A | Cover winding motor | 81 | 91 | FLIR | Normal | Normal | 0 | 70 | 2026-07-30 | 55.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-30 | 48.2
|  |  | Bearing 2 motor | 76 | 86 | FLIR | Normal |  | 0 | 65 | 2026-07-30 | 51.4
|  |  | Bearing 3 pump | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 33.3
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 2.3 | 40 | 2026-07-30 | 42.3
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 39.7
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 39
2 | LJ20PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 2C | Cover winding motor | 81 | 91 | FLIR | Normal | Normal | 0 | 70 | 2026-07-23 | 53.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 42.5
|  |  | Bearing 2 motor | 76 | 86 | FLIR | Normal |  | 0 | 65 | 2026-07-23 | 53.4
|  |  | Bearing 3 pump | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 33.7
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 39.8
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 39.7
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 39.3
2 | LJ20MAG10AP011-001 | EQUIPMENT-VACUUM PUMP 2A | Cover winding motor | 81 | 91 | FLIR | Normal | Normal | 0 | 70 | 2026-07-30 | 53.4 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-30 | 41.6
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-30 | 55.2
|  |  | Bearing 3 pump | 56 | 66 | FLIR | Normal |  | 1 | 45 | 2026-07-30 | 46
|  |  | Bearing 4 pump | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-30 | 44.4
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 1.6 | 40 | 2026-07-30 | 41.6
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0.4 | 40 | 2026-07-30 | 40.4
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 1.4 | 40 | 2026-07-30 | 41.4
2 | LJ20MAG10AP012-001 | EQUIPMENT-VACUUM PUMP 2B | Cover winding motor | 81 | 91 | FLIR | Normal | Medium | 0 | 70 | 2026-07-30 | 54 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-30 | 41.8
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-30 | 53.5
|  |  | Bearing 3 pump | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-30 | 39.9
|  |  | Bearing 4 pump | 56 | 66 | FLIR | Normal |  | 0.9 | 45 | 2026-07-30 | 45.9
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-30 | 38.1
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 2.4 | 40 | 2026-07-30 | 42.4
|  |  | Conection Phasa T | 51 | 61 | FLIR | Medium |  | 11.3 | 40 | 2026-07-30 | 51.3
2 | LJ20MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 2 | Bearing 1 | 101 | 111 | FLIR | Normal | Normal | 0 | 90 | 2026-07-29 | 69 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 2 | 71 | 81 | FLIR | Normal |  | 0.2 | 60 | 2026-07-29 | 60.2
2 | LJ20MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 2 | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-29 | 57.2 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 3 | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-29 | 54
|  |  | Bearing 4 | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-29 | 47.2
2 | LJ20BFT10GT001-001 | EQUIPMENT-LV TRANSFORMER 43T UNIT 2 | Body Timur | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-24 | 38.5 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Barat | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-24 | 40
|  |  | Phasa 6,3 Kv R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 34.8
|  |  | Phasa 6,3 Kv S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 34.3
|  |  | Phasa 6,3 Kv T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 34.3
|  |  | Phasa 380 V R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 39.4
|  |  | Phasa 380 V S | 51 | 61 | FLIR | Normal |  | 0.9 | 40 | 2026-07-24 | 40.9
|  |  | Phasa 380 V T | 51 | 61 | FLIR | Normal |  | 1 | 40 | 2026-07-24 | 41
2 | LJ20BFT10GT002-001 | EQUIPMENT-LV TRANSFORMER 44T UNIT 2 | Body Timur | 46238 | 46248 | FLIR | Normal | Normal | 0 | 50 | 2026-07-24 | 44.9 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Barat | 46238 | 46248 | FLIR | Normal |  | 0 | 50 | 2026-07-24 | 46.5
|  |  | Phasa 6,3 Kv R | 46238 | 46248 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 36
|  |  | Phasa 6,3 Kv S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 35.6
|  |  | Phasa 6,3 Kv T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 36.9
|  |  | Phasa 380 V R | 46238 | 46248 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 36.2
|  |  | Phasa 380 V S | 46238 | 46248 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 39.2
|  |  | Phasa 380 V T | 46238 | 46248 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 39.6
2 | LJ20BFT10GT007-001 | EQUIPMENT- LV TRANSFORMER EXCITATION | Body Timur | 53.1 | 63.1 | FLIR | Normal | Normal | 0 | 50 | 2026-07-24 | 42.1 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Barat | 11 | 21 | FLIR | Normal |  | 0 | 50 | 2026-07-24 | 0
|  |  | Phasa 6,3 Kv R | 38.1 | 48.1 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 27.1
|  |  | Phasa 6,3 Kv S | 39 | 49 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 28
|  |  | Phasa 6,3 Kv T | 38.7 | 48.7 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 27.7
|  |  | Phasa 380 V R | 40.2 | 50.2 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 29.2
|  |  | Phasa 380 V S | 45.6 | 55.6 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 34.6
|  |  | Phasa 380 V T | 39.5 | 49.5 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 28.5
2 | LJ20MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 2 | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 3 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 4 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
2 | LJ20MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 2 | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 3 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 4 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
2 | LJ20BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 34.5 MVA 150/6.3 KV UNIT 2 | Body Transformer sisi Utara | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-22 | 55.9 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Transformer sisi Selatan | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-22 | 50.5
|  |  | Body Transformer sisi Barat | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-22 | 55.5
|  |  | Body Transformer sisi Timur | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-22 | 55.5
|  |  | Bushing Trafo Phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-22 | 36
|  |  | Bushing Trafo Phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-22 | 36.2
|  |  | Bushing Trafo Phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-22 | 36.5
|  |  | Arester Trafo phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-22 | 32.1
|  |  | Arester Trafo phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-22 | 32.8
|  |  | Arester Trafo phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-22 | 31
3 | LJ30LCB10AP001-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3A | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-08 | 43.8 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-08 | 39.8
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-08 | 47.6
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-08 | 40.8
|  |  | Bearing 4 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-08 | 46.4
|  |  | Breaker Contactor | 76 | 86 | FLIR | Low |  | 6.7 | 65 | 2026-07-08 | 71.7
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-08 | 29.7
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-08 | 30.4
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-08 | 26.8
3 | LJ30LCB10AP002-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3B | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-22 | 52.2 | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-22 | 42.9
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-22 | 52.2
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-22 | 50.2
|  |  | Bearing 4 pump | 71 | 81 | FLIR | Normal |  | 1 | 60 | 2026-07-22 | 61
|  |  | Breaker Contactor | 76 | 86 | FLIR | Normal |  | 0.7 | 65 | 2026-07-22 | 65.7
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-22 | 36.4
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-22 | 36.7
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-22 | 37.7
3 | LJ30LCB10AP003-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3C | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-22 | 51 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-22 | 43.3
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-22 | 54.3
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-22 | 42.1
|  |  | Bearing 4 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-22 | 44
|  |  | Breaker Contactor | 76 | 86 | FLIR | Normal |  | 0 | 65 | 2026-07-22 | 60.6
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-22 | 35.1
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-22 | 34.5
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-22 | 35.9
3 | LJ30MAG10AP011-001 | EQUIPMENT-WATER JET PUMP (WJP) 3A | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-08 | 60 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-08 | 45.1
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-08 | 55.5
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-08 | 50.3
|  |  | Bearing 4 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-08 | 51.6
|  |  | Breaker Contactor | 76 | 86 | FLIR | Normal |  | 0 | 65 | 2026-07-08 | 59.7
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 2 | 40 | 2026-07-08 | 42
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-08 | 38.6
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 4 | 40 | 2026-07-08 | 44
3 | LJ30MAG10AP012-001 | EQUIPMENT-WATER JET PUMP (WJP) 3B | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 2 motor | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 3 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 4 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Breaker Contactor | 76 | 86 | FLIR | STD BY |  | STD BY | 65 |  | STD BY
|  |  | Conection Phasa R | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
|  |  | Conection Phasa S | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
|  |  | Conection Phasa T | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
3 | LJ30LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 3A | Cover winding motor | 71 | 81 | FLIR | Normal | Medium | 0 | 60 | 2026-07-22 | 51 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 3.1 | 50 | 2026-07-22 | 53.1
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-22 | 40.1
|  |  | Bearing 3 coupling | 61 | 71 | FLIR | Low |  | 5 | 50 | 2026-07-22 | 55
|  |  | Bearing 4 coupling | 61 | 71 | FLIR | Medium |  | 11 | 50 | 2026-07-22 | 61
|  |  | Bearing 5 pump | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-22 | 49.6
|  |  | Bearing 6 pump | 61 | 71 | FLIR | Normal |  | 3.3 | 50 | 2026-07-22 | 53.3
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-22 | 24
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-22 | 24.1
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-22 | 24
3 | LJ30LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 3B | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 3 coupling | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 4 coupling | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 5 pump | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 6 pump | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Conection Phasa R | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa S | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa T | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
3 | LJ30PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 3A | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-31 | 50.9 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-31 | 37.7
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-31 | 52.9
|  |  | Bearing 3 pump | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-31 | 33.7
|  |  | Bearing 4 pump | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-31 | 32.9
|  |  | Breaker Contactor | 76 | 86 | FLIR | Normal |  | 3.6 | 65 | 2026-07-31 | 68.6
|  |  | Conection Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-31 | 32.2
|  |  | Conection Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-31 | 35.1
|  |  | Conection Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-31 | 32.1
3 | LJ30PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 3B | Cover winding motor | 71 | 81 | FLIR | Normal | Medium | 0 | 60 | 2026-07-31 | 52.8 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-31 | 40.6
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-31 | 55.3
|  |  | Bearing 3 pump | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-31 | 33.3
|  |  | Bearing 4 pump | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-31 | 31.5
|  |  | Breaker Contactor | 76 | 86 | FLIR | Medium |  | 12.3 | 65 | 2026-07-31 | 77.3
|  |  | Conection Phasa R | 51 | 61 | FLIR | Medium |  | 14.5 | 40 | 2026-07-31 | 54.5
|  |  | Conection Phasa S | 51 | 61 | FLIR | Low |  | 5.3 | 40 | 2026-07-31 | 45.3
|  |  | Conection Phasa T | 51 | 61 | FLIR | Low |  | 8.3 | 40 | 2026-07-31 | 48.3
3 | LJ30PGB10AN001-001 | EQUIPMENT-COOLING TOWER FAN 3A | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0.2 | 60 | 2026-07-22 | 60.2 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-22 | 48.2
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-22 | 49.4
|  |  | Bearing 3 fan | 56 | 66 | FLIR | Normal |  | 2.7 | 45 | 2026-07-22 | 47.7
|  |  | Breaker Contactor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-22 | 58.5
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 3.5 | 30 | 2026-07-22 | 33.5
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 3 | 30 | 2026-07-22 | 33
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 3.2 | 30 | 2026-07-22 | 33.2
3 | LJ30PGB10AN002-001 | EQUIPMENT-COOLING TOWER FAN 3B | Cover winding motor | 71 | 81 | FLIR | Normal | Low | 0 | 60 | 2026-07-09 | 55.1 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-09 | 47.2
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-09 | 43.6
|  |  | Bearing 3 fan | 56 | 66 | FLIR | Normal |  | 4.6 | 45 | 2026-07-09 | 49.6
|  |  | Breaker Contactor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-09 | 58.6
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 3 | 30 | 2026-07-09 | 33
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 2.4 | 30 | 2026-07-09 | 32.4
|  |  | Conection Phasa T | 41 | 51 | FLIR | Low |  | 8.2 | 30 | 2026-07-09 | 38.2
3 | LJ30HLB20AN010-001 | EQUIPMENT-SECONDARY AIR FAN UNIT 3 | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-31 | 50.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-31 | 40.6
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-31 | 50
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-31 | 46.9
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 1.5 | 50 | 2026-07-31 | 51.5
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-31 | 23.5
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-31 | 23.4
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-31 | 23.5
3 | LJ30HLB10AN010-001 | EQUIPMENT-PRIMARY AIR FAN UNIT 3 | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 4.7 | 60 | 2026-07-07 | 64.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-07 | 35.7
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-07 | 44.3
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 2.2 | 50 | 2026-07-07 | 52.2
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-07 | 49.4
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-07 | 23.9
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-07 | 24.1
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-07 | 24.1
3 | LJ30HFC10AN011-001 | EQUIPMENT-RECIRCULATING AIR FAN (RAF) 3A | Cover winding motor | 66 | 76 | FLIR | STD BY | STD BY | STD BY | 55 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 3 fan | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 4 fan | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 5 fan | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 6 fan | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Breaker Contactor | 41 | 51 | FLIR | STD BY |  | STD BY | 65 |  | STD BY
|  |  | Conection Phasa R | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa S | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa T | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
3 | LJ30HFC10AN012-001 | EQUIPMENT-RECIRCULATING AIR FAN (RAF) 3B | Cover winding motor | 66 | 76 | FLIR | Normal | Normal | 0 | 55 | 2026-07-07 | 53.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-07 | 38.8
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Normal |  | 3.7 | 55 | 2026-07-07 | 58.7
|  |  | Bearing 3 fan | 66 | 76 | FLIR | Normal |  | 1 | 55 | 2026-07-07 | 56
|  |  | Bearing 4 fan | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-07 | 52.8
|  |  | Bearing 5 fan | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-07 | 53.4
|  |  | Bearing 6 fan | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-07 | 54.4
|  |  | Breaker Contactor | 76 | 86 | FLIR | Normal |  | 4.8 | 65 | 2026-07-07 | 69.8
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 1.3 | 30 | 2026-07-07 | 31.3
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 2.9 | 30 | 2026-07-07 | 32.9
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-07 | 29.8
3 | LJ30HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 3A | Cover winding motor | 81 | 91 | FLIR | Normal | Low | 0 | 70 | 2026-07-21 | 50 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 36.1
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 40.8
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-21 | 45.9
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Low |  | 8 | 50 | 2026-07-21 | 58
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 23.2
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 23.2
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-21 | 23.2
3 | LJ30HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 3B | Cover winding motor | 81 | 91 | FLIR | Normal | Low | 3 | 70 | 2026-07-07 | 73 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-07 | 35.5
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-07 | 39.8
|  |  | Bearing 3 fan | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-07 | 42.6
|  |  | Bearing 4 fan | 61 | 71 | FLIR | Low |  | 9 | 50 | 2026-07-07 | 59
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-07 | 23.5
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-07 | 23.5
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-07 | 23.4
3 | LJ30PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 3A | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 3 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Conection Phasa R | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa S | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
|  |  | Conection Phasa T | 41 | 51 | FLIR | STD BY |  | STD BY | 30 |  | STD BY
3 | LJ30PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 3B | Cover winding motor | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-09 | 57.5 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-09 | 44.3
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-09 | 41.5
|  |  | Bearing 3 pump | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-09 | 51.8
|  |  | Conection Phasa R | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-09 | 22.8
|  |  | Conection Phasa S | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-09 | 23.1
|  |  | Conection Phasa T | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-09 | 23
3 | LJ30GCF10AP007-001 | EQUIPMENT-HIGH PRESURE BWRO PUMP 3A | Cover winding motor | 66 | 76 | FLIR | Normal | Normal | 0 | 55 | 2026-07-31 | 34.2 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-31 | 33.9
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-31 | 33.6
3 | LJ30GCF10AP008-001 | EQUIPMENT-HIGH PRESURE BWRO PUMP 3B | Cover winding motor | 66 | 76 | FLIR | STD BY | - | STD BY | 55 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | - |  |  | 55 |  | STD BY
3 | LJ30GCF10AP001-001 | EQUIPMENT-HIGH PRESURE SWRO PUMP 3A | Cover winding motor | 66 | 76 | FLIR | Normal | Normal | 0 | 55 | 2026-07-31 | 45.4 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-31 | 41.7
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-31 | 40.4
3 | LJ30GCF10AP002-001 | EQUIPMENT-HIGH PRESURE SWRO PUMP 3B | Cover winding motor | 66 | 76 | FLIR | STD BY | STD BY | STD BY | 55 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
3 | LJ30MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 3 | Body generator | 71 | 81 | FLIR | Normal | Medium | 0 | 60 | 2026-07-17 | 53.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 turbin | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-17 | 58.8
|  |  | Shaft bearing 1 turbin | 161 | 171 | FLIR | Normal |  | 0 | 150 | 2026-07-17 | 0
|  |  | Bearing 2 turbin | 66 | 76 | FLIR | Medium |  | 13.6 | 55 | 2026-07-17 | 68.6
|  |  | Shaft bearing 2 turbin | 111 | 121 | FLIR | Normal |  | 0 | 100 | 2026-07-17 | 92.5
|  |  | Bearing 3 generator | 66 | 76 | FLIR | Low |  | 5.4 | 55 | 2026-07-17 | 60.4
|  |  | Shaft bearing 3 generator | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-17 | 51.5
|  |  | Bearing 4 generator | 66 | 76 | FLIR | Normal |  | 0.2 | 55 | 2026-07-17 | 55.2
|  |  | Shaft bearing 4 generator | 66 | 76 | FLIR | Normal |  | 0.8 | 55 | 2026-07-17 | 55.8
3 | LJ30MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 3 | Bearing 1 turbin | 71 | 81 | FLIR | Normal | Medium | 0 | 60 | 2026-07-17 | 58.8 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Shaft bearing 1 turbin | 161 | 171 | FLIR | Normal |  | 0 | 150 | 2026-07-17 | 0
|  |  | Bearing 2 turbin | 66 | 76 | FLIR | Medium |  | 13.6 | 55 | 2026-07-17 | 68.6
|  |  | Shaft bearing 2 turbin | 111 | 121 | FLIR | Normal |  | 0 | 100 | 2026-07-17 | 92.5
3 | LJ30BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 40 MVA 150/6.3 KV UNIT 3 | Body Transformer sisi Utara | 66 | 76 | FLIR | Normal | Normal | 0 | 55 | 2026-07-16 | 45.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Transformer sisi Selatan | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-16 | 45
|  |  | Body Transformer sisi Barat | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-16 | 47
|  |  | Body Transformer sisi Timur | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-16 | 47.2
|  |  | Bushing Trafo Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-16 | 31.6
|  |  | Bushing Trafo Phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-16 | 31.6
|  |  | Bushing Trafo Phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-16 | 30.8
|  |  | Arester Trafo phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-16 | 31.9
|  |  | Arester Trafo phasa S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-16 | 31.8
|  |  | Arester Trafo phasa T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-16 | 31.6
3 | LJ30BBT10GT001-001 | EQUIPMENT-UNIT AUXILIARY TRANSFORMER (UAT) 6.3 MVA UNIT 3 | Body Auxiliary sisi Utara | 66 | 76 | FLIR | Normal | Normal | 0 | 55 | 2026-07-31 | 45.2 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Auxiliary sisi Selatan | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-31 | 44.8
|  |  | Body Auxiliary sisi Barat | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-31 | 41.1
|  |  | Body Auxiliary sisi Timur | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-31 | 53.7
|  |  | Bushing Primary Phasa R | 51 | 61 | FLIR | Normal |  | 0.8 | 40 | 2026-07-31 | 40.8
|  |  | Bushing Primary Phasa S | 51 | 61 | FLIR | Normal |  | 0.4 | 40 | 2026-07-31 | 40.4
|  |  | Bushing Primary Phasa T | 51 | 61 | FLIR | Normal |  | 1.6 | 40 | 2026-07-31 | 41.6
|  |  | Bushing Secondary Phasa R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-31 | 38.5
|  |  | Bushing Secondary Phasa S | 51 | 61 | FLIR | Normal |  | 1.8 | 40 | 2026-07-31 | 41.8
|  |  | Bushing Secondary Phasa T | 51 | 61 | FLIR | Normal |  | 1.2 | 40 | 2026-07-31 | 41.2
|  |  | Bushing Secondary Phasa N | 51 | 61 | FLIR | Normal |  | 1.3 | 40 | 2026-07-31 | 41.3
3 | LJ00SGA10AP002-001 | EQUIPMENT-JOCKEY PUMP 3A | Cover winding motor | 66 | 76 | FLIR | Normal | Normal | 0 | 55 | 2026-07-16 | 31.7 | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-16 | 30.1
|  |  | Bearing 2 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-16 | 34.3
3 | LJ00SGA10AP003-001 | EQUIPMENT-JOCKEY PUMP 3B | Cover winding motor | 66 | 76 | FLIR | STD BY | STD BY | STD BY | 55 |  | STD BY
|  |  | Bearing 1 motor | 61 | 71 | FLIR | STD BY |  | STD BY | 50 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
3 | LJ00SGA10AP001-001 | EQUIPMENT-FIRE FIGHTING PUMP WITH MOTOR UNIT 3 | Cover winding motor | 71 | 81 | FLIR | Normal | Medium | 0 | 60 | 2026-07-16 | 32 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-16 | 33.2
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-16 | 30.8
|  |  | Bearing 3 pump | 51 | 61 | FLIR | Low |  | 8.7 | 40 | 2026-07-16 | 48.7
|  |  | Bearing 4 pump | 51 | 61 | FLIR | Medium |  | 19.4 | 40 | 2026-07-16 | 59.4
3 | LJ00SGA10AP004-001 | EQUIPMENT-FIRE FIGHTING PUMP WITH DIESEL MOTOR UNIT 3 | Body motor | 111 | 121 | FLIR | Normal | Normal | 0 | 100 | 2026-07-16 | 90.1 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 111 | 121 | FLIR | Normal |  | 0 | 100 | 2026-07-16 | 64.1
|  |  | Bearing 2 motor | 111 | 121 | FLIR | Normal |  | 0 | 100 | 2026-07-16 | 59.1
|  |  | Bearing 3 pump | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-16 | 37.4
|  |  | Bearing 4 pump | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-16 | 33.8
3 | LJ30BFA10GT003-001 | EQUIPMENT- LV TRANSFORMER HSB | Body Utara | 66 | 76 | FLIR | Normal | Normal | 0 | 55 | 2026-07-23 | 33.7 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Selatan | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-23 | 33.5
|  |  | Phasa 6,3 Kv R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 31.3
|  |  | Phasa 6,3 Kv S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 31.1
|  |  | Phasa 6,3 Kv T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 30
|  |  | Phasa 380 V R | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 33
|  |  | Phasa 380 V S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 32.4
|  |  | Phasa 380 V T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 31.8
3 | LJ30BFA10GT002-001 | EQUIPMENT- LV TRANSFORMER 40.B | Body Timur | 66 | 76 | FLIR | Normal | Normal | 0 | 55 | 2026-07-23 | 37.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Barat | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-23 | 37.3
|  |  | Phasa 6,3 Kv R | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-23 | 34.6
|  |  | Phasa 6,3 Kv S | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-23 | 33.9
|  |  | Phasa 6,3 Kv T | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-23 | 34.6
|  |  | Phasa 380 V R | 66 | 76 | FLIR | Normal |  | 0 | 55 | 2026-07-23 | 37.9
|  |  | Phasa 380 V S | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 34.4
|  |  | Phasa 380 V T | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 32.7
3 | LJ30BFA10GT001-001 | EQUIPMENT- LV TRANSFORMER 41.B | Body Utara R | 66 | 76 | FLIR | STD BY | STD BY | STD BY | 55 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Body Utara S | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Body Utara T | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Body Selatan R | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Body Selatan S | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Body Selatan T | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Phasa 6,3 Kv R | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
|  |  | Phasa 6,3 Kv S | 51 | 61 | FLIR | STD BY |  | STD BY | 40 |  | STD BY
3 | LJ30MAV10AP004-001 | EQUIPMENT-JACKING OIL PUMP 1 UNIT 3 | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
3 | LJ30MAV10AP005-001 | EQUIPMENT-JACKING OIL PUMP 2 UNIT 3 | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
3 | LJ30MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 3 | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 3 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 4 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
3 | LJ30MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 3 | Cover winding motor | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Bearing 1 motor | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Bearing 2 motor | 66 | 76 | FLIR | STD BY |  | STD BY | 55 |  | STD BY
|  |  | Bearing 3 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bearing 4 pump | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
0 | LJ00EBA40AF001-001 | EQUIPMENT-BELT CONVEYOR 4.1 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-23 | 45.5 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 37.9
|  |  | Bearing 2 motor | 51 | 61 | FLIR | Normal |  | 4.3 | 40 | 2026-07-23 | 44.3
|  |  | Bearing 3 drive pulley | 51 | 61 | FLIR | Normal |  | 3 | 40 | 2026-07-23 | 43
|  |  | Bearing 4 drive pulley | 41 | 51 | FLIR | Normal |  | 4.1 | 30 | 2026-07-23 | 34.1
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 1 | 30 | 2026-07-23 | 31
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0.2 | 30 | 2026-07-23 | 30.2
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 1.1 | 30 | 2026-07-23 | 31.1
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 1.1 | 30 | 2026-07-23 | 31.1
|  |  | Conection panel | 81 | 91 | FLIR | Normal |  | 0 | 70 | 2026-07-23 | 68.9
0 | LJ00EBA40AF002-001 | EQUIPMENT-BELT CONVEYOR 4.2 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-23 | 46.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 37.6
|  |  | Bearing 2 motor | 51 | 61 | FLIR | Normal |  | 4.9 | 40 | 2026-07-23 | 44.9
|  |  | Bearing 3 drive pulley | 51 | 61 | FLIR | Normal |  | 4.4 | 40 | 2026-07-23 | 44.4
|  |  | Bearing 4 drive pulley | 41 | 51 | FLIR | Normal |  | 4.7 | 30 | 2026-07-23 | 34.7
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 2.4 | 30 | 2026-07-23 | 32.4
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0.9 | 30 | 2026-07-23 | 30.9
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 1.5 | 30 | 2026-07-23 | 31.5
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 1.4 | 30 | 2026-07-23 | 31.4
|  |  | Conection panel | 81 | 91 | FLIR | Normal |  | 0 | 70 | 2026-07-23 | 69.2
0 | LJ00EBA50AF001-001 | EQUIPMENT-BELT CONVEYOR 5.1 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-24 | 37 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 35.2
|  |  | Bearing 2 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 33.7
|  |  | Bearing 3 drive pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 36.1
|  |  | Bearing 4 drive pulley | 41 | 51 | FLIR | Normal |  | 0.5 | 30 | 2026-07-24 | 30.5
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 29.2
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0.6 | 30 | 2026-07-24 | 30.6
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 29.9
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0.9 | 30 | 2026-07-24 | 30.9
|  |  | Conection panel | 81 | 91 | FLIR | Normal |  | 0 | 70 | 2026-07-24 | 0
0 | LJ00EBA50AF002-001 | EQUIPMENT-BELT CONVEYOR 5.2 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 |  | 42.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 33.9
|  |  | Bearing 2 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 37
|  |  | Bearing 3 drive pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 33.5
|  |  | Bearing 4 drive pulley | 41 | 51 | FLIR | Normal |  | 2.2 | 30 | 2026-07-23 | 32.2
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 1.3 | 30 | 2026-07-23 | 31.3
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0.4 | 30 | 2026-07-23 | 30.4
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 1.5 | 30 | 2026-07-23 | 31.5
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 1.5 | 30 | 2026-07-23 | 31.5
|  |  | Conection panel | 81 | 91 | FLIR | Normal |  | 0 | 70 | 2026-07-23 | 0
0 | LJ00EBA60AF001-001 | EQUIPMENT-BELT CONVEYOR 7.1 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-24 | 40.5 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 33.2
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-24 | 38.9
|  |  | Bearing 3 drive pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 37.9
|  |  | Bearing 4 drive pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 29.8
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0.6 | 30 | 2026-07-24 | 30.6
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0.5 | 30 | 2026-07-24 | 30.5
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 29.3
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 29.9
|  |  | Conection panel | 81 | 91 | FLIR | Normal |  | 0 | 70 | 2026-07-24 | 69.7
0 | LJ00EBA60AF002-001 | EQUIPMENT-BELT CONVEYOR 7.2 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-23 | 34 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 31.4
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 31.8
|  |  | Bearing 3 drive pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 33.8
|  |  | Bearing 4 drive pulley | 41 | 51 | FLIR | Normal |  | 3.5 | 30 | 2026-07-23 | 33.5
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 2.3 | 30 | 2026-07-23 | 32.3
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 3.1 | 30 | 2026-07-23 | 33.1
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 29.8
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0.4 | 30 | 2026-07-23 | 30.4
|  |  | Conection panel | 81 | 91 | FLIR | Normal |  | 0 | 70 | 2026-07-23 | 69.7
0 | LJ00EBA70AF001-001 | EQUIPMENT-BELT CONVEYOR 8.1 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-24 | 41.4 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 1.3 | 40 | 2026-07-24 | 41.3
|  |  | Bearing 2 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 38.2
|  |  | Bearing 3 drive pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 35.8
|  |  | Bearing 4 drive pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 38.7
|  |  | Bearing snap pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 37.3
|  |  | Bearing snap pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 38.3
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 28.2
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 27.7
|  |  | Conection panel | 81 | 91 | FLIR | Normal |  | 0.1 | 70 | 2026-07-24 | 70.1
0 | LJ00EBA70AF002-001 | EQUIPMENT-BELT CONVEYOR 8.2 | Cover winding motor | 61 | 71 | FLIR | Normal | Medium | 4.6 | 50 | 2026-07-23 | 54.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Low |  | 7.7 | 40 | 2026-07-23 | 47.7
|  |  | Bearing 2 motor | 51 | 61 | FLIR | Medium |  | 11 | 40 | 2026-07-23 | 51
|  |  | Bearing 3 drive pulley | 51 | 61 | FLIR | Normal |  | 3 | 40 | 2026-07-23 | 43
|  |  | Bearing 4 drive pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 35.1
|  |  | Bearing snap pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 35.1
|  |  | Bearing snap pulley | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 33.8
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 26.7
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 26.6
|  |  | Conection panel | 81 | 91 | FLIR | Normal |  | 4 | 70 | 2026-07-23 | 74
0 | LJ00EBA80AF001-001 | EQUIPMENT-BELT CONVEYOR 10.1 | Cover winding motor | 56 | 66 | FLIR | Normal | Normal | 0 | 45 | 2026-07-24 | 34.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-24 | 33.9
|  |  | Bearing 2 motor | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-24 | 32.9
|  |  | Bearing 3 drive pulley | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-24 | 32.7
|  |  | Bearing 4 drive pulley | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-24 | 31.4
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 29.2
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 28.9
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 27.6
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-24 | 28
0 | LJ00EBA80AF002-001 | EQUIPMENT-BELT CONVEYOR 10.2 | Cover winding motor | 56 | 66 | FLIR | Normal | Normal | 0 | 45 | 2026-07-23 | 39.8 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 37.9
|  |  | Bearing 2 motor | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 36.8
|  |  | Bearing 3 drive pulley | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 35.8
|  |  | Bearing 4 drive pulley | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 39.9
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 29.6
|  |  | Bearing snap pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 29.6
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 27
|  |  | Bearing tail pulley | 41 | 51 | FLIR | Normal |  | 0 | 30 | 2026-07-23 | 26.1
0 | LJ00EBC10AT003-001 | EQUIPMENT-CRUSHER 1 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-23 | 39.4 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 34.2
|  |  | Bearing 2 motor | 71 | 81 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 33.9
|  |  | Bearing 3 crusher | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-23 | 36
|  |  | Bearing 4 crusher | 51 | 61 | FLIR | Normal |  | 0 | 60 | 2026-07-23 | 43.1
|  |  | Conection Phasa R | 46 | 56 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 32
|  |  | Conection Phasa S | 46 | 56 | FLIR | Normal |  | 0 | 35 | 2026-07-23 | 32.4
|  |  | Conection Phasa T | 46 | 56 | FLIR | Normal |  | 0 | 35 | 2026-07-23 | 33.7
0 | LJ00EBC10AT004-001 | EQUIPMENT-CRUSHER 2 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-23 | 40.5 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 35.9
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 38
|  |  | Bearing 3 crusher | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-23 | 34.8
|  |  | Bearing 4 crusher | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-23 | 37.9
|  |  | Conection Phasa R | 46 | 56 | FLIR | Normal |  | 0 | 35 | 2026-07-23 | 32.4
|  |  | Conection Phasa S | 46 | 56 | FLIR | Normal |  | 0 | 35 | 2026-07-23 | 32.8
|  |  | Conection Phasa T | 46 | 56 | FLIR | Normal |  | 0 | 35 | 2026-07-23 | 32.8
0 | LJ00EBC10AT001-001 | EQUIPMENT-ROLLING SCREEN 1 | Cover winding motor | 51 | 61 | FLIR | Normal | Normal | 0 | 40 | 2026-07-23 | 37.3 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 32.5
|  |  | Bearing 2 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 34.5
|  |  | Gear box | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 44.3
0 | LJ00EBC10AT002-001 | EQUIPMENT-ROLLING SCREEN 2 | Cover winding motor | 51 | 61 | FLIR | Normal | Normal | 0 | 40 | 2026-07-23 | 38.9 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 33
|  |  | Bearing 2 motor | 51 | 61 | FLIR | Normal |  | 0 | 40 | 2026-07-23 | 35.1
|  |  | Gear box | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 46.1
0 | LJ00EBA40AT001-001 | EQUIPMENT-VIBRATING FEEDER 1 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-24 | 46.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-24 | 37.6
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-24 | 32.5
|  |  | Gear box Bearing 1 | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-24 | 36.3
|  |  | Gear box Bearing 2 | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-24 | 35.7
0 | LJ00EBA40AT002-001 | EQUIPMENT-VIBRATING FEEDER 2 | Cover winding motor | 61 | 71 | FLIR | Normal | Normal | 0 | 50 | 2026-07-23 | 47.1 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Bearing 1 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 39.2
|  |  | Bearing 2 motor | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 43.4
|  |  | Gear box Bearing 1 | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 37
|  |  | Gear box Bearing 2 | 61 | 71 | FLIR | Normal |  | 0 | 50 | 2026-07-23 | 36
0 | LJ00BBA10GT001-001 | EQUIPMENT-TRANSFORMER COAL HANDLING 1 | Body Transformer sisi Utara | 71 | 81 | FLIR | STD BY | STD BY | STD BY | 60 |  | STD BY | Equipment dalam keadaan standby saat rutin PDM dilakukan.
|  |  | Body Transformer sisi Selatan | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Body Transformer sisi Barat | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Body Transformer sisi Timur | 71 | 81 | FLIR | STD BY |  | STD BY | 60 |  | STD BY
|  |  | Bushing Primary Phasa R | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Bushing Primary Phasa S | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Bushing Primary Phasa T | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Secondary Phasa R | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Secondary Phasa S | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Secondary Phasa T | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
|  |  | Secondary Phasa N | 56 | 66 | FLIR | STD BY |  | STD BY | 45 |  | STD BY
0 | LJ00BBA10GT002-001 | EQUIPMENT-TRANSFORMER COAL HANDLING 2 | Body Transformer sisi Utara | 71 | 81 | FLIR | Normal | Normal | 0 | 60 | 2026-07-23 | 45.6 | Keterangan : Tidak ada hotspot / kenaikan temperature yang berbahaya. Rekomendasi : Lakukan pengukuran thermography sesuai 52 week.
|  |  | Body Transformer sisi Selatan | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-23 | 45.4
|  |  | Body Transformer sisi Barat | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-23 | 46.3
|  |  | Body Transformer sisi Timur | 71 | 81 | FLIR | Normal |  | 0 | 60 | 2026-07-23 | 43.8
|  |  | Bushing Primary Phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 36.1
|  |  | Bushing Primary Phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 36.8
|  |  | Bushing Primary Phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 36.1
|  |  | Secondary Phasa R | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 33.3
|  |  | Secondary Phasa S | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 33.9
|  |  | Secondary Phasa T | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 33.9
|  |  | Secondary Phasa N | 56 | 66 | FLIR | Normal |  | 0 | 45 | 2026-07-23 | 33

## Sheet1
LJ10PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 1A
LJ10PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 1B
LJ10LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 1A
LJ10LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 1B
LJ10HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 1A
LJ10HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 1B
LJ10HLB10AN001-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 1A
LJ10HLB10AN002-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 1B
LJ10HLB10AN003-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 1A
LJ10HLB10AN004-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 1B
LJ10LCB10AP010-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 1A
LJ10LCB10AP020-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 1B
LJ10PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 1A
LJ10PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 1B
LJ10MAG10AP011-001 | EQUIPMENT-VACUUM PUMP 1A
LJ10MAG10AP012-001 | EQUIPMENT-VACUUM PUMP 1B
LJ10GCK10AP005-001 | EQUIPMENT-BWRO PUMP 1A
LJ10GCK10AP006-001 | EQUIPMENT-BWRO PUMP 1B
LJ10GCK10AP007-001 | EQUIPMENT-HIGH PRESSURE SWRO PUMP 1A
LJ10GCK10AP008-001 | EQUIPMENT-HIGH PRESSURE SWRO PUMP 1B
LJ10MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 1
LJ10MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 1
LJ10BFT10GT001-001 | EQUIPMENT-LV TRANSFORMER 43T UNIT 1
LJ10BFT10GT002-001 | EQUIPMENT-LV TRANSFORMER 44T UNIT 1
LJ10BFT10GT007-001 | EQUIPMENT- LV TRANSFORMER EXCITATION
LJ10MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 1
LJ10MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 1
LJ10BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 34.5 MVA 150/6.3 KV UNIT 1
LJ10BBT10GT002-001 | EQUIPMENT-TRANSFORMER ASH HANDLING 1
LJ10BBT10GT003-001 | EQUIPMENT-TRANSFORMER ASH HANDLING 2
LJ20PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 2A
LJ20PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 2B
LJ20LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 2A
LJ20LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 2B
LJ20HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 2A
LJ20HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 2B
LJ20HLB10AN001-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 2A
LJ20HLB10AN002-001 | EQUIPMENT-PRIMARY AIR FAN (PAF) 2B
LJ20HLB10AN003-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 2A
LJ20HLB10AN004-001 | EQUIPMENT-SECONDARY AIR FAN (SAF) 2B
LJ20LCB10AP010-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 2A
LJ20LCB10AP020-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 2B
LJ20PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 2A
LJ20PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 2B
LJ20MAG10AP011-001 | EQUIPMENT-VACUUM PUMP 2A
LJ20MAG10AP012-001 | EQUIPMENT-VACUUM PUMP 2B
LJ20MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 2
LJ20MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 2
LJ20BFT10GT001-001 | EQUIPMENT-LV TRANSFORMER 43T UNIT 2
LJ20BFT10GT002-001 | EQUIPMENT-LV TRANSFORMER 44T UNIT 2
LJ20BFT10GT007-001 | EQUIPMENT- LV TRANSFORMER EXCITATION
LJ20MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 2
LJ20MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 2
LJ20BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 34.5 MVA 150/6.3 KV UNIT 2
LJ30LCB10AP001-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3A
LJ30LCB10AP002-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3B
LJ30LCB10AP003-001 | EQUIPMENT-CONDENSATE EXTRACTION PUMP (CEP) 3C
LJ30MAG10AP011-001 | EQUIPMENT-WATER JET PUMP (WJP) 3A
LJ30MAG10AP012-001 | EQUIPMENT-WATER JET PUMP (WJP) 3B
LJ30LAC10AP001-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 3A
LJ30LAC10AP002-001 | EQUIPMENT-BOILER FEEDWATER PUMP (BFP) 3B
LJ30PGB10AP001-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 3A
LJ30PGB10AP002-001 | EQUIPMENT-CLOSED COOLING CIRCULATING WATER PUMP (C3WP) 3B
LJ30PGB10AN001-001 | EQUIPMENT-COOLING TOWER FAN 3A
LJ30PGB10AN002-001 | EQUIPMENT-COOLING TOWER FAN 3B
LJ30HLB20AN010-001 | EQUIPMENT-SECONDARY AIR FAN UNIT 3
LJ30HLB10AN010-001 | EQUIPMENT-PRIMARY AIR FAN UNIT 3
LJ30HFC10AN011-001 | EQUIPMENT-RECIRCULATING AIR FAN (RAF) 3A
LJ30HFC10AN012-001 | EQUIPMENT-RECIRCULATING AIR FAN (RAF) 3B
LJ30HNC10AN001-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 3A
LJ30HNC10AN002-001 | EQUIPMENT-INDUCE DRAUGHT FAN (IDF) 3B
LJ30PAC10AP001-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 3A
LJ30PAC10AP002-001 | EQUIPMENT-CIRCULATING WATER PUMP (CWP) 3B
LJ30GCF10AP007-001 | EQUIPMENT-HIGH PRESURE BWRO PUMP 3A
LJ30GCF10AP008-001 | EQUIPMENT-HIGH PRESURE BWRO PUMP 3B
LJ30GCF10AP001-001 | EQUIPMENT-HIGH PRESURE SWRO PUMP 3A
LJ30GCF10AP002-001 | EQUIPMENT-HIGH PRESURE SWRO PUMP 3B
LJ30MKA10AG001-001 | EQUIPMENT-GENERATOR UNIT 3
LJ30MAA10HB010-001 | EQUIPMENT-HP TURBINE ASSEMBLY UNIT 3
LJ30BAT10GT001-001 | EQUIPMENT-GENERATOR TRANSFORMER (GT) 40 MVA 150/6.3 KV UNIT 3
LJ30BBT10GT001-001 | EQUIPMENT-UNIT AUXILIARY TRANSFORMER (UAT) 6.3 MVA UNIT 3
LJ00SGA10AP002-001 | EQUIPMENT-JOCKEY PUMP 3A
LJ00SGA10AP003-001 | EQUIPMENT-JOCKEY PUMP 3B
LJ00SGA10AP001-001 | EQUIPMENT-FIRE FIGHTING PUMP WITH MOTOR UNIT 3
LJ00SGA10AP004-001 | EQUIPMENT-FIRE FIGHTING PUMP WITH DIESEL MOTOR UNIT 3
LJ30BFA10GT003-001 | EQUIPMENT- LV TRANSFORMER HSB
LJ30BFA10GT002-001 | EQUIPMENT- LV TRANSFORMER 40.B
LJ30BFA10GT001-001 | EQUIPMENT- LV TRANSFORMER 41.B
LJ30MAV10AP004-001 | EQUIPMENT-JACKING OIL PUMP 1 UNIT 3
LJ30MAV10AP005-001 | EQUIPMENT-JACKING OIL PUMP 2 UNIT 3
LJ30MAV10AP001-001 | EQUIPMENT-AC LUBE OIL PUMP UNIT 3
LJ30MAV10AP003-001 | EQUIPMENT-DC LUBE OIL PUMP UNIT 3
LJ00EBA40AF001-001 | EQUIPMENT-BELT CONVEYOR 4.1
LJ00EBA40AF002-001 | EQUIPMENT-BELT CONVEYOR 4.2
LJ00EBA50AF001-001 | EQUIPMENT-BELT CONVEYOR 5.1
LJ00EBA50AF002-001 | EQUIPMENT-BELT CONVEYOR 5.2
LJ00EBA60AF001-001 | EQUIPMENT-BELT CONVEYOR 7.1
LJ00EBA60AF002-001 | EQUIPMENT-BELT CONVEYOR 7.2
LJ00EBA70AF001-001 | EQUIPMENT-BELT CONVEYOR 8.1
LJ00EBA70AF002-001 | EQUIPMENT-BELT CONVEYOR 8.2
LJ00EBA80AF001-001 | EQUIPMENT-BELT CONVEYOR 10.1
LJ00EBA80AF002-001 | EQUIPMENT-BELT CONVEYOR 10.2
LJ00EBC10AT003-001 | EQUIPMENT-CRUSHER 1
LJ00EBC10AT004-001 | EQUIPMENT-CRUSHER 2
LJ00EBC10AT001-001 | EQUIPMENT-ROLLING SCREEN 1
LJ00EBC10AT002-001 | EQUIPMENT-ROLLING SCREEN 2
LJ00EBA40AT001-001 | EQUIPMENT-VIBRATING FEEDER 1
LJ00EBA40AT002-001 | EQUIPMENT-VIBRATING FEEDER 2
LJ00BBA10GT001-001 | EQUIPMENT-TRANSFORMER COAL HANDLING 1
LJ00BBA10GT002-001 | EQUIPMENT-TRANSFORMER COAL HANDLING 2